## Dashboard
DT-3 ENERGY CONSUMPTION & EPI PERFORMANCE DASHBOARD (JAN - JUL 2025 vs 2026)
2026 JAN-JUL AVG EPI |  | EPI VARIANCE (vs 2025) |  | NET YTD COST SAVINGS |  |  | NET YTD ENERGY SAVED
Status: Best-in-Class / Efficient |  | Improved YTD Performance |  | Jan–July 2026 vs 2025 |  |  | Facility Energy Reduction
1. EPI PERFORMANCE LEVEL BENCHMARK STANDARDS (kWh/m²/year) |  |  |  | 2. DT3 MONTHLY ENERGY CONSUMPTION & EPI TREND (2025 vs 2026 INCL. JULY)
Performance Level | EPI Range (kWh/m²/yr) | Status Category | Facility Benchmark Target | Month | 2025 Cons (kWh) | 2026 Cons (kWh) | 2025 EPI (kWh/m²/yr) | 2026 EPI (kWh/m²/yr) | Variance (EPI)
Average | 160 – 200 | Typical Office | Standard Commercial Building | Jan
Good | 120 – 150 | Efficient Office | Energy Efficient Facility Target | Feb
Excellent | Below 120 | Best-in-Class | DT3 Operational Target (<120) | Mar
Apr
May
Jun
Jul
Jan-Jul AVERAGE
3. YoY SAVINGS & COMPARATIVE PERFORMANCE ANALYSIS TABLE (JAN - JUL 2025 vs 2026)
Energy Component | 2025 Cons (kWh) | 2026 Cons (kWh) | kWh Savings | % Change (kWh) | 2025 Cost (₹) | 2026 Cost (₹) | Net Cost Savings (₹) | % Cost Savings | Operational Analysis & Savings Justification
EB Electricity (kWh) | [8 empty] | 23,622 kWh EB Savings (-6.2%) achieved YTD via efficiency
AHU HVAC Power (kWh) | [8 empty] | Transitioned to 12*5.5 KAM model from May (saved ~4,035 kWh/mo)
DG Backup Power (kWh) | [8 empty] | DG run hours reduced by 37.8% due to higher utility grid stability
BTU Cooling Load (kWh) | [8 empty] | BTU cooling load energy reduced by 35,641 kWh (-18.3%) saving ₹3.83L
Total Facility (Jan-Jul) | [8 empty] | Total Jan–July facility energy cost reduced by ₹5.45L (-9.8%)
4. KEY OPERATIONAL INSIGHTS & SAVINGS JUSTIFICATION (DT3)
• Operational Model Transition: |  | Prior to May, DT3 AHUs operated on a 24*7 running schedule. From May onwards, DT3 transitioned to a 12*5.5 KAM model (12 hrs/day, 5.5 days/week), discontinuing night operations and weekend shifts.
• Hours & Energy Saved: |  | Switching to the 12*5.5 KAM model saved ~12 hrs/day on weekdays and full weekends (~434 operating hrs/mo per AHU, totaling ~1,736 AHU hrs/mo saved). Monthly AHU consumption dropped from 10,301 kWh in April to 6,266 kWh in May (saved 4,035 kWh / -39.2%), 7,682 kWh in June, and 8,308 kWh in July.
• EPI Trend Justification (vs 2025): |  | Annualized EPI dropped significantly YTD (May EPI: 100.42 vs 123.85 in 2025, -18.9%; June EPI: 108.28 vs 139.05 in 2025, -22.1%; July EPI: 147.21 vs 150.36 in 2025). Overall Jan–Jul average EPI improved from 119.36 to 110.39 kWh/m²/yr (-7.5%), maintaining Best-in-Class status (<120 kWh/m²/yr).
• YTD Cost Savings: |  | Total Jan–July energy cost fell from ₹55.51L in 2025 to ₹50.06L in 2026, delivering ₹5.45L (-9.8%) cost savings YTD.

## Mar-24
March - 2024
Sr.No | Location | Meter | Previous Reading | 2024-03-01 | 2024-03-02 | 2024-03-03 | 2024-03-04 | 2024-03-05 | 2024-03-06 | 2024-03-07 | 2024-03-08 | 2024-03-09 | 2024-03-10 | 2024-03-11 | 2024-03-12 | 2024-03-13 | 2024-03-14 | 2024-03-15 | 2024-03-16 | 2024-03-17 | 2024-03-18 | 2024-03-19 | 2024-03-20 | 2024-03-21 | 2024-03-22 | 2024-03-23 | 2024-03-24 | 2024-03-25 | 2024-03-26 | 2024-03-27 | 2024-03-28 | 2024-03-29 | 2024-03-30 | 2024-03-31 | Consumption
|  |  |  | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 |  | SL No 540430038840 (EB Unit) | 6604 | 6890 | 7077 | 7264 | 7501 | 7740 | 8016 | 8260 | 8503 | 8721 | 8938 | 9166 | 9432 | 9675 | 9922 | 10128 | 10324 | 10542 | 10788 | 11051 | 11305 | 11563 | 11784 | 11987 | 12185 | 12392 | 12629 | 12859 | 13093 | 13317 | 13516 | 13613
|  | DG | 165 | 218 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 258 | 271 | 271 | 271 | 271 | 271 | 271 | 272 | 272 | 272 | 272 | 272 | 272 | 272 | 272 | 272 | 278 | 278
2 |  | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
3 |  | SL No 540430038844 (EB Unit) | 16819 | 17196 | 17459 | 17701 | 18037 | 18363 | 18729 | 19110 | 19460 | 19746 | 20030 | 20356 | 20729 | 21071 | 21423 | 21703 | 21962 | 22246 | 22598 | 22978 | 23334 | 23707 | 24010 | 24269 | 24524 | 24795 | 25118 | 25438 | 25765 | 26060 | 26319 | 26440
|  | DG | 352 | 430 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 433 | 491 | 508 | 508 | 508 | 508 | 508 | 508 | 508 | 508 | 508 | 508 | 508 | 508 | 508 | 508 | 508 | 517 | 517
4 |  | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 |  | SL No 540430038849 (EB Unit) | 2670 | 2868 | 2973 | 3077 | 3235 | 3404 | 3602 | 3782 | 3944 | 4053 | 4163 | 4319 | 4493 | 4656 | 4826 | 4956 | 5048 | 5170 | 5340 | 5518 | 5697 | 5870 | 6024 | 6138 | 6241 | 6359 | 6496 | 6649 | 6811 | 6975 | 7097 | 7150
|  | DG | 76 | 120 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 149 | 154 | 154 | 154 | 154 | 154 | 154 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 159 | 159
6 |  | SL No 540430038696 (EB Unit) | 7208 | 7489 | 7616 | 7747 | 7999 | 8168 | 8384 | 8618 | 8862 | 9031 | 9157 | 9390 | 9632 | 9846 | 10087 | 10280 | 10419 | 10545 | 10792 | 11047 | 11291 | 11527 | 11717 | 11844 | 11930 | 12027 | 12230 | 12449 | 12650 | 12826 | 12947 | 13012
|  | DG | 171 | 231 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 232 | 284 | 299 | 299 | 299 | 299 | 299 | 299 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
7 |  | SL No 540430038843 (EB Unit) | 29055 | 30140 | 30900 | 31689 | 32526 | 33424 | 34380 | 35165 | 35988 | 36654 | 37387 | 38168 | 39015 | 39822 | 40654 | 41394 | 42060 | 42788 | 43574 | 44408 | 45244 | 46076 | 46872 | 47586 | 48246 | 48812 | 49605 | 50402 | 51220 | 52028 | 52719 | 53008
|  | DG | 733 | 899 | 904 | 904 | 904 | 904 | 904 | 904 | 904 | 904 | 904 | 904 | 904 | 904 | 1018 | 1069 | 1069 | 1069 | 1069 | 1069 | 1069 | 1071 | 1071 | 1071 | 1071 | 1071 | 1071 | 1071 | 1071 | 1071 | 1088 | 1088
8 |  | SL No 540430038848 (EB Unit) | 12402 | 12517 | 12635 | 12703 | 12814 | 12913 | 13033 | 13109 | 13209 | 13286 | 13390 | 13444 | 13578 | 13604 | 13679 | 13743 | 13819 | 13866 | 13957 | 14045 | 14134 | 14245 | 14376 | 14488 | 14603 | 14696 | 14849 | 14966 | 15108 | 15239 | 15398 | 15438
|  | DG | 199 | 223 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 239 | 244 | 244 | 244 | 244 | 244 | 244 | 244 | 244 | 244 | 244 | 244 | 244 | 244 | 244 | 244 | 248 | 248
1 |  | AHU1 | 2568 | 2760 | 2851 | 2952 | 3098 | 3248 | 3398 | 3546 | 3682 | 3771 | 3807 | 3953 | 4051 | 4130 | 4212 | 4274 | 4333 | 4333 | 4423 | 4540 | 4648 | 4727 | 4809 | 4847 | 4847 | 4867 | 4960 | 5065 | 5165 | 5237 | 5270 | 5270
|  | DG | 132 | 149 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 169 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 173 | 173
|  | AHU2 | 2698 | 2834 | 2899 | 2974 | 3076 | 3183 | 3289 | 3401 | 3508 | 3571 | 3597 | 3702 | 3787 | 3872 | 3956 | 4019 | 4079 | 4079 | 4185 | 4264 | 4351 | 4430 | 4507 | 4548 | 4548 | 4567 | 4700 | 4781 | 4861 | 4972 | 4964 | 4964
|  | DG | 146 | 155 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 157 | 175 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
3 |  | AHU3 | 1243 | 1356 | 1406 | 1463 | 1542 | 1624 | 1704 | 1791 | 1868 | 1929 | 1947 | 2031 | 2096 | 2156 | 2229 | 2279 | 2291 | 2291 | 2332 | 2382 | 2449 | 2524 | 2568 | 2594 | 2594 | 2603 | 2653 | 2688 | 2759 | 2813 | 2862 | 2862
|  | DG | 110 | 116 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129 | 129
4 |  | AHU4 | 1283 | 1379 | 1447 | 1526 | 1641 | 1763 | 1886 | 2004 | 2125 | 2195 | 2225 | 2345 | 2436 | 2506 | 2549 | 2615 | 2666 | 2666 | 2760 | 2900 | 2975 | 3047 | 3114 | 3148 | 3148 | 3166 | 3249 | 3346 | 3441 | 3541 | 3541 | 3542
|  | DG | 89 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
1 |  | AHU1 - BTU | 5741.69 | 6562.41 | 6890.24 | 7282.68 | 7893.82 | 8306.92 | 8908.75 | 9501.28 | 10331.83 | 10745.79 | 10745.79 | 11168.93 | 11708.3 | 12136.9 | 12869.71 | 13327.98 | 13568.36 | 13568.36 | 14217.95 | 14758.62 | 15349.21 | 15938.04 | 16487.56 | 16808.03 | 16808.03 | 16954.4 | 17718.62 | 18500.95 | 19332.58 | 19974.08 | 20397.69 | 20397.69
2 |  | AHU2 - BTU | 6755.88 | 7661.86 | 7970.73 | 8408.61 | 9031.46 | 9433.95 | 10030.26 | 10656.22 | 11185.27 | 11390.86 | 11390.86 | 12035.86 | 12685.61 | 13185.76 | 13843.29 | 14301.4 | 14565.24 | 14565.24 | 15266.35 | 15829.21 | 16319.61 | 16865.69 | 17424.86 | 17763.58 | 17763.58 | 17961 | 18768.58 | 19529.06 | 20169.14 | 20744.31 | 21181.85 | 21181.85
3 |  | AHU3 - BTU | 4835 | 5667.86 | 5917.95 | 6264.13 | 6574.83 | 6724.38 | 6951.63 | 7380.45 | 7862.22 | 7978.5 | 7978.9 | 8330.4 | 8737.58 | 9120.95 | 9614.02 | 9927.43 | 10088.81 | 10088.81 | 10492.87 | 10968.6 | 11428.92 | 11964.02 | 12414.02 | 12678.79 | 12678.79 | 12842.42 | 13440.25 | 14006.83 | 14679.97 | 15144.65 | 15520.6 | 15520.6
4 |  | AHU4 - BTU | 7375.29 | 8046.26 | 8406.3 | 8918.24 | 9381.07 | 9718.97 | 10254.25 | 10874.39 | 11696.27 | 12671 | 12671 | 12735.79 | 13446.2 | 13979.11 | 14862.99 | 15297.68 | 15611.68 | 15611.68 | 16410.86 | 17079.15 | 17746.73 | 18455.13 | 19011.66 | 19435.86 | 19435.86 | 19788.02 | 20748.15 | 21703.67 | 22555.75 | 23394.23 | 24009.78 | 24009.78
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
|  | Total Power - EB Unit | [33 empty] | EB
|  | Total Power- DG | [33 empty] | AHU
|  | Total Power Cumulative | [33 empty] | BTU
DG
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3
DG
4 | 3F | AHU4
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## Apr-24
April - 2024
Sr.No | Location | Meter | Previous Reading | 2024-04-01 | 2024-04-02 | 2024-04-03 | 2024-04-04 | 2024-04-05 | 2024-04-06 | 2024-04-07 | 2024-04-08 | 2024-04-09 | 2024-04-10 | 2024-04-11 | 2024-04-12 | 2024-04-13 | 2024-04-14 | 2024-04-15 | 2024-04-16 | 2024-04-17 | 2024-04-18 | 2024-04-19 | 2024-04-20 | 2024-04-21 | 2024-04-22 | 2024-04-23 | 2024-04-24 | 2024-04-25 | 2024-04-26 | 2024-04-27 | 2024-04-28 | 2024-04-29 | 2024-04-30 | Consumption
|  |  |  | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 |  | SL No 540430038840 (EB Unit) |  | 13954 | 14192 | 14447 | 14695 | 14934 | 15140 | 15340 | 15616 | 15857 | 16102 | 16352 | 16577 | 16833 | 17031 | 17277 | 17515 | 17761 | 18010 | 18263 | 18443 | 18647 | 18895 | 19148 | 19397 | 19626 | 19862 | 20081 | 20271 | 20513 | 20652
|  | DG |  | 278 | 278 | 284 | 284 | 284 | 284 | 284 | 284 | 286 | 296 | 296 | 296 | 296 | 301 | 304 | 304 | 304 | 304 | 304 | 304 | 304 | 304 | 306 | 306 | 308 | 319 | 323 | 323 | 323 | 328
2 |  | SL No 540430038845 (EB Unit) |  | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG |  | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
3 |  | SL No 540430038844 (EB Unit) |  | 26903 | 27234 | 27600 | 27954 | 28285 | 28564 | 28848 | 29211 | 29553 | 29896 | 30245 | 30561 | 30813 | 31065 | 31409 | 31746 | 32095 | 32436 | 32782 | 33017 | 33274 | 33623 | 33981 | 34335 | 34646 | 34977 | 35264 | 35509 | 35851 | 36049
|  | DG |  | 517 | 517 | 526 | 526 | 526 | 526 | 526 | 526 | 528 | 544 | 544 | 544 | 544 | 550 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 555 | 557 | 557 | 560 | 576 | 581 | 581 | 581 | 588
4 |  | SL No 540430038821 (EB Unit) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 |  | SL No 540430038849 (EB Unit) |  | 7390 | 7565 | 7733 | 7902 | 8061 | 8178 | 8290 | 8458 | 8615 | 8778 | 8941 | 9098 | 9203 | 9314 | 9484 | 9651 | 9822 | 9981 | 10131 | 10221 | 10330 | 10496 | 10645 | 10818 | 10970 | 11120 | 11234 | 11348 | 11505 | 11588
|  | DG |  | 159 | 159 | 163 | 163 | 163 | 163 | 163 | 163 | 164 | 174 | 174 | 174 | 174 | 177 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 181 | 181 | 183 | 191 | 193 | 193 | 193 | 196
6 |  | SL No 540430038696 (EB Unit) |  | 13245 | 13458 | 13668 | 13921 | 14166 | 14326 | 14459 | 14714 | 14957 | 15185 | 15437 | 15699 | 15835 | 15970 | 16209 | 16435 | 16658 | 16892 | 17148 | 17274 | 17415 | 17674 | 17939 | 18217 | 18491 | 18754 | 18932 | 19098 | 19384 | 19531
|  | DG |  | 300 | 300 | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 321 | 321 | 321 | 321 | 326 | 329 | 329 | 329 | 329 | 329 | 329 | 329 | 329 | 331 | 331 | 332 | 345 | 347 | 347 | 347 | 353
7 |  | SL No 540430038843 (EB Unit) |  | 54181 | 54950 | 55754 | 56487 | 57283 | 57971 | 58639 | 59399 | 60160 | 60923 | 61715 | 62483 | 63168 | 63819 | 64541 | 65298 | 66081 | 66869 | 67698 | 68306 | 68961 | 69739 | 70532 | 71312 | 72055 | 72822 | 73539 | 74244 | 74950 | 75336
|  | DG |  | 1088 | 1088 | 1101 | 1101 | 1101 | 1101 | 1101 | 1101 | 1104 | 1134 | 1134 | 1134 | 1134 | 1152 | 1159 | 1159 | 1159 | 1159 | 1159 | 1159 | 1159 | 1159 | 1166 | 1166 | 1170 | 1203 | 1212 | 1212 | 1212 | 1226
8 |  | SL No 540430038848 (EB Unit) |  | 15690 | 15807 | 15919 | 15996 | 16074 | 16153 | 16225 | 16309 | 16399 | 16485 | 16570 | 16653 | 16722 | 16789 | 16899 | 17020 | 17152 | 17244 | 17333 | 17390 | 17459 | 17536 | 17595 | 17658 | 17719 | 17782 | 17836 | 17874 | 17935 | 17963
|  | DG |  | 248 | 248 | 250 | 250 | 250 | 250 | 250 | 250 | 251 | 255 | 255 | 255 | 255 | 257 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 259 | 260 | 260 | 261 | 265 | 268 | 268 | 268 | 269
1 |  | AHU1 |  | 5326 | 5383 | 5441 | 5502 | 5558 | 5596 | 5596 | 5660 | 5719 | 5814 | 5921 | 6026 | 6086 | 6086 | 6197 | 6304 | 6413 | 6519 | 6620 | 6680 | 6680 | 6800 | 6913 | 7010 | 7078 | 7142 | 7161 | 7162 | 7229 | 7266
|  | DG |  | 173 | 173 | 174 | 174 | 174 | 174 | 174 | 174 | 175 | 178 | 178 | 178 | 178 | 178 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 181 | 181 | 181 | 182 | 182 | 182 | 182 | 184
2 |  | AHU2 |  | 5045 | 5128 | 5216 | 5303 | 5366 | 5407 | 5407 | 5482 | 5585 | 5634 | 5684 | 5739 | 5769 | 5769 | 5853 | 5927 | 6001 | 6073 | 6134 | 6161 | 6161 | 6215 | 6266 | 6328 | 6395 | 6453 | 6480 | 6480 | 6548 | 6581
|  | DG |  | 178 | 117 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 188 | 188 | 188 | 188 | 188 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 190 | 190 | 190 | 192 | 192 | 192 | 192 | 194
3 |  | AHU3 |  | 2937 | 3007 | 3081 | 3157 | 3223 | 3277 | 3277 | 3323 | 3418 | 3505 | 3568 | 3633 | 3691 | 3691 | 3773 | 3882 | 3923 | 4000 | 4073 | 4114 | 4114 | 4203 | 4280 | 4359 | 4425 | 4485 | 4505 | 4505 | 4567 | 4607
|  | DG |  | 129 | 129 | 131 | 131 | 131 | 131 | 131 | 131 | 131 | 135 | 135 | 135 | 135 | 135 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 137 | 137 | 137 | 139 | 139 | 139 | 139 | 140
4 |  | AHU4 |  | 3629 | 3722 | 3802 | 3880 | 3942 | 3976 | 3976 | 4026 | 4070 | 4101 | 4131 | 4177 | 4195 | 4195 | 4246 | 4278 | 4311 | 4344 | 4385 | 4422 | 4422 | 4503 | 4581 | 4660 | 4725 | 4786 | 4806 | 4806 | 4889 | 4928
|  | DG |  | 117 | 117 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 121 | 121 | 121 | 121 | 121 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 123 | 123 | 123 | 125 | 125 | 125 | 125 | 127
1 |  | AHU1 - BTU |  | 21409.6 | 22161.77 | 22850.5 | 23503.28 | 24067.02 | 24424.25 | 24424.25 | 25188.51 | 25950.06 | 26827.08 | 27672.48 | 28403.37 | 28668.95 | 28668.95 | 29756.55 | 30722.75 | 31506.4 | 32311.93 | 32993.25 | 33324.88 | 33324.88 | 34423.33 | 35423.46 | 36245.63 | 37031.83 | 37699.55 | 38117.54 | 38117.54 | 39198.41 | 39808.33
2 |  | AHU2 - BTU |  | 21945.98 | 22720.54 | 23411.95 | 24120.47 | 24773.43 | 25081.65 | 25081.65 | 26091.01 | 26746.39 | 27447.98 | 28122.32 | 28720.23 | 29040.22 | 29040.22 | 29905.93 | 30619.39 | 31315.45 | 32035.07 | 32730.58 | 33108.49 | 33108.49 | 34097.47 | 34888.69 | 35580.02 | 36264.12 | 36972.64 | 37406.7 | 37406.7 | 38410.78 | 39039.43
3 |  | AHU3 - BTU |  | 16330.66 | 16953.07 | 17517.78 | 18145.78 | 18720.58 | 19061.88 | 19061.88 | 19705 | 20386.96 | 21064.88 | 21798.73 | 22392.31 | 22683.07 | 22683.07 | 23805.99 | 24672.94 | 25738.12 | 26399.51 | 27163.83 | 27621.63 | 27621.63 | 28699.69 | 29733.84 | 30553.78 | 31401.06 | 32233.52 | 32758.82 | 32758.82 | 33732.59 | 34466.31
4 |  | AHU4 - BTU |  | 25419.59 | 26370.92 | 27234.14 | 28024.3 | 28788.29 | 29255.67 | 29255.67 | 30254.33 | 31229.2 | 32263.49 | 33125.05 | 33971.68 | 34364.35 | 34364.35 | 35632.68 | 36573.12 | 37463.45 | 38302.71 | 39055.22 | 39535.63 | 39535.63 | 41006.37 | 42325.41 | 43455.98 | 44476.59 | 45418.41 | 46087.97 | 46087.97 | 47630.79 | 48593.12
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [31 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit) | [32 empty] | EB
|  | DG | [32 empty] | AHU
7 | 3F | SL No 540430038843 (EB Unit) | [32 empty] | BTU
|  | DG | [32 empty] | DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3
DG
4 | 3F | AHU4
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## May-24
May - 2024
Sr.No | Location | Meter | Previous Reading | 2024-05-01 | 2024-05-02 | 2024-05-03 | 2024-05-04 | 2024-05-05 | 2024-05-06 | 2024-05-07 | 2024-05-08 | 2024-05-09 | 2024-05-10 | 2024-05-11 | 2024-05-12 | 2024-05-13 | 2024-05-14 | 2024-05-15 | 2024-05-16 | 2024-05-17 | 2024-05-18 | 2024-05-19 | 2024-05-20 | 2024-05-21 | 2024-05-22 | 2024-05-23 | 2024-05-24 | 2024-05-25 | 2024-05-26 | 2024-05-27 | 2024-05-28 | 2024-05-29 | 2024-05-30 | 2024-05-31 | Consumption
|  |  |  | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 20652 | 21014 | 21267 | 21509 | 21714 | 21934 | 22136 | 22375 | 22572 | 22809 | 23008 | 23204 | 23430 | 23596 | 23844 | 24100 | 24354 | 24495 | 24682 | 24968 | 25142 | 25402 | 25630 | 25817 | 26049 | 26251 | 26443 | 26672 | 26889 | 27095 | 27328 | 27418
|  | DG | 328 | 328 | 328 | 328 | 328 | 328 | 369 | 382 | 455 | 455 | 505 | 518 | 518 | 599 | 613 | 613 | 613 | 700 | 700 | 727 | 798 | 798 | 798 | 864 | 880 | 882 | 889 | 915 | 955 | 999 | 1025 | 1040
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
3 | 3F | SL No 540430038844 (EB Unit) | 36049 | 36569 | 36928 | 37268 | 37536 | 37819 | 38104 | 38443 | 38717 | 39054 | 39326 | 39382 | 39877 | 40110 | 40457 | 40827 | 41189 | 41374 | 41653 | 41899 | 42140 | 42499 | 42821 | 43077 | 43396 | 43656 | 43897 | 44220 | 44524 | 44805 | 45128 | 45249
|  | DG | 588 | 588 | 588 | 588 | 588 | 588 | 651 | 671 | 781 | 781 | 856 | 873 | 873 | 997 | 1017 | 1017 | 1017 | 1158 | 1158 | 1182 | 1286 | 1286 | 1286 | 1885 | 1409 | 1411 | 1420 | 1461 | 1523 | 1588 | 1627 | 1649
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 11588 | 11830 | 11992 | 12152 | 12247 | 12341 | 12478 | 12640 | 12758 | 12919 | 13043 | 13141 | 13253 | 13364 | 13533 | 13708 | 13887 | 13969 | 14074 | 14183 | 14304 | 14491 | 14655 | 14790 | 14957 | 15079 | 15195 | 15366 | 15528 | 15675 | 15845 | 15905
|  | DG | 196 | 196 | 196 | 196 | 196 | 196 | 225 | 237 | 291 | 291 | 326 | 332 | 332 | 395 | 404 | 404 | 404 | 482 | 482 | 492 | 543 | 543 | 543 | 600 | 613 | 614 | 619 | 641 | 674 | 713 | 734 | 746
6 | 3F | SL No 540430038696 (EB Unit) | 19531 | 19954 | 20225 | 20489 | 20660 | 20844 | 21069 | 21335 | 21521 | 21728 | 21896 | 22015 | 22167 | 22338 | 22615 | 22899 | 23186 | 23327 | 23527 | 23699 | 23908 | 24186 | 24418 | 24591 | 24803 | 24944 | 25085 | 25335 | 25563 | 25780 | 26023 | 26115
|  | DG | 353 | 353 | 353 | 353 | 353 | 353 | 402 | 417 | 492 | 492 | 559 | 564 | 564 | 659 | 673 | 673 | 673 | 807 | 807 | 825 | 916 | 916 | 916 | 891 | 1011 | 1011 | 1016 | 1045 | 1085 | 1150 | 1185 | 1209
7 | 3F | SL No 540430038843 (EB Unit) | 75336 | 76453 | 77223 | 77941 | 78535 | 79195 | 79781 | 80472 | 81019 | 81713 | 82317 | 82909 | 83577 | 84046 | 84747 | 85477 | 86207 | 86599 | 87217 | 87733 | 88230 | 88988 | 89665 | 90201 | 90898 | 91441 | 91754 | 92396 | 93063 | 93673 | 94361 | 94630
|  | DG | 1226 | 1226 | 1226 | 1226 | 1226 | 1226 | 1350 | 1366 | 1590 | 1590 | 1741 | 1778 | 1778 | 2018 | 2048 | 2048 | 2048 | 2340 | 2340 | 2390 | 2581 | 2581 | 2581 | 2792 | 2844 | 2848 | 2859 | 2934 | 3042 | 3170 | 3251 | 3299
8 | 3F | SL No 540430038848 (EB Unit) | 17963 | 18048 | 18105 | 18160 | 18203 | 18257 | 18308 | 18364 | 18415 | 18521 | 18600 | 18702 | 18797 | 18874 | 18939 | 19005 | 19076 | 19116 | 19201 | 19292 | 19366 | 19515 | 19662 | 19754 | 19907 | 20039 | 20174 | 20315 | 20466 | 20554 | 20659 | 20693
|  | DG | 269 | 269 | 269 | 269 | 269 | 269 | 277 | 282 | 306 | 306 | 321 | 330 | 330 | 361 | 364 | 364 | 364 | 405 | 405 | 414 | 440 | 440 | 440 | 431 | 498 | 498 | 504 | 526 | 551 | 572 | 580 | 585
1 | 3F | AHU1 | 7266 | 7368 | 7437 | 7504 | 7531 | 7531 | 7585 | 7648 | 7684 | 7753 | 7780 | 7821 | 7821 | 7867 | 7966 | 8069 | 8164 | 8184 | 8242 | 8242 | 8317 | 8411 | 8497 | 8543 | 8622 | 8622 | 8622 | 8726 | 8812 | 8884 | 8982 | 9012
|  | DG | 184 | 184 | 184 | 184 | 184 | 184 | 195 | 200 | 229 | 229 | 247 | 249 | 249 | 299 | 305 | 305 | 305 | 363 | 363 | 363 | 398 | 398 | 398 | 443 | 454 | 454 | 454 | 472 | 496 | 524 | 543 | 555
2 | 3F | AHU2 | 6581 | 6675 | 6754 | 6820 | 6845 | 6845 | 6898 | 6961 | 6997 | 7066 | 7100 | 7132 | 7132 | 7181 | 7273 | 7367 | 7453 | 7486 | 7529 | 7529 | 7608 | 7693 | 7778 | 7824 | 7900 | 7900 | 7900 | 7999 | 8089 | 8165 | 8263 | 8291
|  | DG | 194 | 194 | 194 | 194 | 194 | 194 | 206 | 211 | 239 | 239 | 255 | 257 | 257 | 317 | 321 | 321 | 321 | 369 | 369 | 369 | 402 | 402 | 402 | 437 | 447 | 447 | 447 | 463 | 488 | 517 | 544 | 557
3 | 3F | AHU3 | 4607 | 4713 | 4807 | 4901 | 4938 | 4938 | 5000 | 5060 | 5095 | 5164 | 5187 | 5227 | 5227 | 5278 | 5379 | 5478 | 5581 | 5603 | 5641 | 5641 | 5705 | 5805 | 5909 | 5951 | 6040 | 6040 | 6040 | 6139 | 6226 | 6301 | 6403 | 6422
|  | DG | 140 | 140 | 140 | 140 | 140 | 140 | 152 | 156 | 183 | 183 | 198 | 199 | 199 | 258 | 264 | 264 | 264 | 324 | 324 | 324 | 356 | 356 | 356 | 395 | 407 | 407 | 407 | 425 | 450 | 481 | 501 | 513
4 | 3F | AHU4 | 4928 | 5053 | 5136 | 5217 | 5248 | 5248 | 5316 | 5388 | 5430 | 5515 | 5553 | 5590 | 5590 | 5628 | 5683 | 5753 | 5834 | 5863 | 5908 | 5908 | 5968 | 6050 | 6134 | 6176 | 6234 | 6234 | 6235 | 6315 | 6389 | 6445 | 6525 | 6551
|  | DG | 127 | 127 | 127 | 127 | 127 | 127 | 140 | 146 | 179 | 179 | 197 | 199 | 199 | 237 | 240 | 240 | 240 | 290 | 290 | 290 | 320 | 320 | 320 | 358 | 363 | 363 | 363 | 378 | 400 | 424 | 441 | 451
1 | 3F | AHU1 - BTU | 39808.33 | 40784.95 | 41523.35 | 42144.42 | 42515.66 | 42515.66 | 43641.97 | 44516.37 | 45377.14 | 46379.68 | 47271.64 | 47689.75 | 47689.75 | 48882.43 | 49887.7 | 50839.03 | 51761.8 | 52601.28 | 53049.22 | 53049.22 | 54218.4 | 55235.63 | 56227.29 | 57193.07 | 58087.18 | 58087.18 | 58087.18 | 59613.06 | 60665.69 | 61550.68 | 62364.23 | 62776
2 | 3F | AHU2 - BTU | 39039.43 | 40011.29 | 40707.58 | 41355.74 | 41673.19 | 41673.19 | 42584.56 | 43444.33 | 44406.91 | 45373.01 | 46278.07 | 46702.92 | 46702.92 | 47791.44 | 48823.62 | 49685.21 | 50511.93 | 51384.4 | 51844.09 | 51844.09 | 53106.22 | 54088.33 | 55133.66 | 56040.25 | 57035.63 | 57035.63 | 57035.63 | 58367.6 | 59509.96 | 60564.32 | 61617.73 | 62028
3 | 3F | AHU3 - BTU | 34466.31 | 35393.85 | 36282.87 | 36977.18 | 37332.32 | 37332.32 | 38473.21 | 39518.46 | 40611.79 | 41664.29 | 42556.38 | 42981.82 | 42981.82 | 44183.84 | 45360.7 | 46420.36 | 47396.84 | 48367.81 | 48970.9 | 48970.9 | 50278.82 | 51264.83 | 52289.15 | 53158.33 | 54071.12 | 54071.12 | 54071.12 | 55480.6 | 56735.68 | 57867.99 | 59125.33 | 59574
4 | 3F | AHU4 - BTU | 48593.12 | 49926.47 | 50835.05 | 51496.28 | 51944.19 | 51944.19 | 53331.66 | 54608.03 | 55899.29 | 57002.08 | 58195.11 | 58725.28 | 58725.28 | 60242.6 | 61701.04 | 63006.1 | 64142.44 | 65039.01 | 65593.76 | 65593.76 | 67007.79 | 68291.96 | 69574.21 | 70699.45 | 71782.99 | 71782.99 | 71782.99 | 73417.79 | 74799.6 | 75826.22 | 76962.14 | 77455
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
|  | Total Power - EB Unit | [33 empty] | EB
|  | Total Power- DG | [33 empty] | AHU
|  | Total Power Cumulative | [33 empty] | BTU
DG
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3
DG
4 | 3F | AHU4
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## June-24
June - 2024
Sr.No | Location | Meter | Previous Reading | 2024-06-01 | 2024-06-02 | 2024-06-03 | 2024-06-04 | 2024-06-05 | 2024-06-06 | 2024-06-07 | 2024-06-08 | 2024-06-09 | 2024-06-10 | 2024-06-11 | 2024-06-12 | 2024-06-13 | 2024-06-14 | 2024-06-15 | 2024-06-16 | 2024-06-17 | 2024-06-18 | 2024-06-19 | 2024-06-20 | 2024-06-21 | 2024-06-22 | 2024-06-23 | 2024-06-24 | 2024-06-25 | 2024-06-26 | 2024-06-27 | 2024-06-28 | 2024-06-29 | 2024-06-30 | Consumption
|  |  |  | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 27418 | 27721 | 27934 | 28120 | 28377 | 28592 | 28856 | 29126 | 29326 | 29543 | 29775 | 29902 | 30131 | 30315 | 30478 | 30690 | 30905 | 31102 | 31284 | 31479 | 31744 | 31999 | 32217 | 32437 | 32667 | 32929 | 33190 | 33458 | 33658 | 33879 | 33984
|  | DG | 1040 | 1078 | 1079 | 1155 | 1155 | 1197 | 1200 | 1207 | 1207 | 1230 | 1230 | 1365 | 1388 | 1465 | 1540 | 1540 | 1547 | 1575 | 1647 | 1700 | 1700 | 1700 | 1700 | 1700 | 1708 | 1708 | 1708 | 1708 | 1745 | 1751 | 1753
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
3 | 3F | SL No 540430038844 (EB Unit) | 45249 | 45659 | 45937 | 46190 | 46554 | 46857 | 47224 | 47560 | 47822 | 48099 | 48444 | 48610 | 48936 | 49185 | 49405 | 49691 | 49960 | 50224 | 50483 | 50770 | 51135 | 51492 | 51774 | 52068 | 52408 | 52771 | 53138 | 53521 | 53797 | 54090 | 54227
|  | DG | 1649 | 1702 | 1702 | 1821 | 1821 | 1885 | 1885 | 1898 | 1898 | 1928 | 1928 | 2127 | 2163 | 2280 | 2392 | 2393 | 2402 | 2439 | 2548 | 2630 | 2630 | 2630 | 2630 | 2630 | 2642 | 2642 | 2642 | 2642 | 2690 | 2699 | 2701
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 15905 | 16093 | 16220 | 16350 | 16538 | 16695 | 16889 | 17062 | 17186 | 17308 | 17492 | 17582 | 17758 | 17891 | 18002 | 18126 | 18248 | 18357 | 18492 | 18644 | 18838 | 19028 | 19149 | 19281 | 19453 | 19612 | 19874 | 20029 | 20170 | 20286 | 20339
|  | DG | 746 | 778 | 779 | 840 | 840 | 878 | 878 | 884 | 884 | 897 | 897 | 1003 | 1021 | 1086 | 1150 | 1150 | 1154 | 1169 | 1229 | 1274 | 1274 | 1274 | 1274 | 1274 | 1280 | 1280 | 1280 | 1280 | 1306 | 1310 | 1311
6 | 3F | SL No 540430038696 (EB Unit) | 26115 | 26384 | 26500 | 26639 | 26918 | 27154 | 27410 | 27656 | 27794 | 27913 | 28193 | 28316 | 28575 | 28764 | 28921 | 29072 | 29219 | 29363 | 29534 | 29756 | 29993 | 30229 | 30340 | 30479 | 30679 | 30924 | 31175 | 31411 | 31599 | 31714 | 31779
|  | DG | 1209 | 1253 | 1253 | 1385 | 1385 | 1381 | 1381 | 1387 | 1387 | 1402 | 1402 | 1567 | 1595 | 1699 | 1795 | 1796 | 1798 | 1814 | 1880 | 1954 | 1954 | 1954 | 1954 | 1954 | 1962 | 1962 | 1962 | 1962 | 1997 | 1998 | 1999
7 | 3F | SL No 540430038843 (EB Unit) | 94630 | 95345 | 95647 | 96151 | 96894 | 97460 | 98176 | 98863 | 99306 | 99658 | 100341 | 100699 | 101318 | 101804 | 102235 | 102687 | 103226 | 103503 | 103957 | 104485 | 105126 | 105778 | 106120 | 106434 | 107025 | 107634 | 108302 | 109015 | 109562 | 109901 | 109964
|  | DG | 3299 | 3414 | 3417 | 3625 | 3625 | 3748 | 3755 | 3770 | 3770 | 3825 | 3825 | 4156 | 4214 | 4426 | 4652 | 4654 | 4669 | 4713 | 4875 | 5018 | 5018 | 5018 | 5018 | 5018 | 5037 | 5037 | 5037 | 5037 | 5108 | 5117 | 5120
8 | 3F | SL No 540430038848 (EB Unit) | 20693 | 20827 | 20964 | 21109 | 21208 | 21287 | 21376 | 21459 | 21570 | 21691 | 21790 | 21831 | 21916 | 21990 | 22049 | 22166 | 22310 | 22431 | 22562 | 22660 | 22787 | 22919 | 23046 | 23171 | 23340 | 23459 | 23580 | 23712 | 23806 | 23926 | 23959
|  | DG | 585 | 606 | 606 | 659 | 659 | 681 | 681 | 684 | 684 | 695 | 695 | 746 | 757 | 789 | 837 | 837 | 844 | 862 | 918 | 945 | 945 | 945 | 945 | 945 | 950 | 950 | 950 | 950 | 964 | 969 | 969
1 | 3F | AHU1 | 9012 | 9122 | 9122 | 9191 | 9295 | 9369 | 9480 | 9594 | 9652 | 9652 | 9758 | 9811 | 9899 | 9960 | 10010 | 10063 | 10063 | 10079 | 10158 | 10241 | 10350 | 10477 | 10547 | 10547 | 10671 | 10740 | 10786 | 10832 | 10880 | 10907 | 10907
|  | DG | 555 | 569 | 569 | 618 | 618 | 645 | 645 | 645 | 645 | 645 | 645 | 708 | 721 | 765 | 814 | 814 | 814 | 817 | 854 | 889 | 889 | 889 | 889 | 889 | 895 | 895 | 895 | 895 | 895 | 895 | 895
2 | 3F | AHU2 | 8291 | 8400 | 8400 | 8467 | 8569 | 8641 | 8743 | 8853 | 8904 | 8904 | 9004 | 9058 | 9115 | 9206 | 9253 | 9302 | 9302 | 9319 | 9400 | 9484 | 9583 | 9691 | 9750 | 9750 | 9871 | 9951 | 10088 | 10191 | 10274 | 10321 | 10321
|  | DG | 557 | 570 | 570 | 620 | 620 | 646 | 646 | 646 | 646 | 646 | 646 | 703 | 716 | 758 | 804 | 804 | 804 | 807 | 847 | 881 | 881 | 881 | 881 | 881 | 887 | 887 | 887 | 887 | 901 | 903 | 903
3 | 3F | AHU3 | 6422 | 6497 | 6497 | 6570 | 6701 | 6788 | 6912 | 7034 | 7096 | 7096 | 7251 | 7272 | 7372 | 7436 | 7492 | 7555 | 7555 | 7615 | 7688 | 7776 | 7943 | 8026 | 8078 | 8078 | 8230 | 8287 | 8496 | 8611 | 8709 | 8764 | 8764
|  | DG | 513 | 526 | 526 | 580 | 580 | 611 | 611 | 611 | 611 | 611 | 611 | 611 | 698 | 748 | 805 | 805 | 805 | 821 | 862 | 898 | 898 | 898 | 898 | 898 | 905 | 905 | 905 | 905 | 920 | 923 | 923
4 | 3F | AHU4 | 6551 | 6630 | 6630 | 6692 | 6793 | 6868 | 6978 | 7085 | 7139 | 7139 | 7243 | 7292 | 7377 | 7433 | 7480 | 7530 | 7530 | 7545 | 7616 | 7693 | 7802 | 7919 | 7986 | 7986 | 8095 | 8214 | 8327 | 8430 | 8530 | 8579 | 8579
|  | DG | 451 | 462 | 462 | 508 | 508 | 535 | 535 | 535 | 535 | 535 | 535 | 596 | 609 | 651 | 698 | 698 | 698 | 701 | 748 | 779 | 779 | 779 | 779 | 779 | 782 | 782 | 782 | 782 | 782 | 782 | 782
1 | 3F | AHU1 - BTU | 62776 | 63415.3 | 63415.3 | 64687.43 | 65634.89 | 66522.4 | 67373.61 | 68037.21 | 68409.19 | 68409.19 | 69562.86 | 70512.77 | 71437.11 | 72406.66 | 73361.83 | 73721.98 | 73721.98 | 73944.72 | 75322.51 | 76461.31 | 77396.6 | 78264.44 | 78656.69 | 78656.69 | 79900.68 | 80881.07 | 81864.67 | 82534.66 | 83015.77 | 83302.6 | 83302.6
2 | 3F | AHU2 - BTU | 62028 | 63002.02 | 63002.02 | 64235.15 | 65387.7 | 66379.9 | 67397.52 | 68114.47 | 68579.72 | 68579.72 | 69776 | 70748.59 | 71773.78 | 72813.4 | 73814.2 | 74316.18 | 74316.18 | 74539.87 | 75969.07 | 77218.15 | 78319.98 | 79132.32 | 79602.03 | 79602.03 | 80744.96 | 81636.5 | 82386.82 | 83051.76 | 83735.66 | 84127.73 | 84127.73
3 | 3F | AHU3 - BTU | 59574 | 60582.14 | 60582.14 | 62065.93 | 63397.48 | 64499.3 | 65751.36 | 66618.02 | 67148.85 | 67148.85 | 68540.02 | 69698.91 | 70933.18 | 72124.93 | 73346.75 | 73930.93 | 73930.98 | 74802.4 | 76401.81 | 77931.25 | 79219.38 | 80305.75 | 80966.66 | 80966.66 | 82450.55 | 83632.35 | 84643.13 | 85751.11 | 86631.9 | 87129.6 | 87129.6
4 | 3F | AHU4 - BTU | 77455 | 78394.88 | 78394.88 | 79937.1 | 81217.59 | 82374.16 | 83373.36 | 84215 | 84687.52 | 84687.52 | 86124.02 | 87339.08 | 88509.81 | 89616.66 | 90758.29 | 91225.51 | 91225.51 | 91587.2 | 92879.84 | 94492.9 | 95697.21 | 96783.15 | 97280.16 | 97280.16 | 98756.31 | 100013.38 | 101081.27 | 102125.13 | 103048.49 | 103444.13 | 103444.13
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [31 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit) | [32 empty] | EB
|  | DG | [32 empty] | AHU
7 | 3F | SL No 540430038843 (EB Unit) | [32 empty] | BTU
|  | DG | [32 empty] | DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3
DG
4 | 3F | AHU4
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## July 24
July 2024
Sr.No | Location | Meter | Previous Reading | 2024-07-01 | 2024-07-02 | 2024-07-03 | 2024-07-04 | 2024-07-05 | 2024-07-06 | 2024-07-07 | 2024-07-08 | 2024-07-09 | 2024-07-10 | 2024-07-11 | 2024-07-12 | 2024-07-13 | 2024-07-14 | 2024-07-15 | 2024-07-16 | 2024-07-17 | 2024-07-18 | 2024-07-19 | 2024-07-20 | 2024-07-21 | 2024-07-22 | 2024-07-23 | 2024-07-24 | 2024-07-25 | 2024-07-26 | 2024-07-27 | 2024-07-28 | 2024-07-29 | 2024-07-30 | 2024-07-31 | Consumption
|  |  |  | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 33984 | 34325 | 34584 | 34840 | 35100 | 35331 | 35537 | 35740 | 35959 | 36232 | 36449 | 36753 | 36947 | 37103 | 37319 | 37550 | 37775 | 37903 | 38256 | 38475 | 38686 | 38886 | 39150 | 39390 | 39651 | 39894 | 40133 | 40341 | 40563 | 40784 | 40954 | 41074
|  | DG | 1753 | 1793 | 1793 | 1793 | 1793 | 1800 | 1818 | 1835 | 1866 | 1866 | 1917 | 1930 | 1979 | 2044 | 2044 | 2059 | 2097 | 2131 | 2131 | 2150 | 2165 | 2165 | 2165 | 2177 | 2177 | 2188 | 2188 | 2190 | 2190 | 2240 | 2322 | 2322
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 54227 | 54698 | 55071 | 55397 | 55806 | 56139 | 56404 | 56666 | 56981 | 57374 | 57683 | 58011 | 58281 | 58486 | 58767 | 59102 | 59418 | 59731 | 60102 | 60404 | 60682 | 60942 | 61319 | 61660 | 62030 | 62370 | 62705 | 62980 | 63280 | 63580 | 63817 | 63982
|  | DG | 2701 | 2764 | 2764 | 2764 | 2764 | 2776 | 2799 | 2820 | 2868 | 2868 | 2945 | 2965 | 3032 | 3117 | 3117 | 3138 | 3197 | 3249 | 3249 | 3276 | 3296 | 3296 | 3296 | 3315 | 3315 | 3332 | 3332 | 3334 | 3334 | 3413 | 3540 | 3540
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 20339 | 20559 | 20750 | 20951 | 21177 | 21350 | 21455 | 21572 | 21747 | 21951 | 22107 | 22283 | 22427 | 22521 | 22633 | 22803 | 22963 | 23120 | 23315 | 23472 | 23572 | 23676 | 23884 | 24077 | 24280 | 24465 | 24642 | 24754 | 24872 | 25020 | 25136 | 25219
|  | DG | 1311 | 1346 | 1346 | 1346 | 1346 | 1352 | 1363 | 1372 | 1412 | 1412 | 1451 | 1464 | 1498 | 1534 | 1534 | 1546 | 1579 | 1610 | 1610 | 1628 | 1637 | 1637 | 1637 | 1650 | 1650 | 1660 | 1660 | 1660 | 1660 | 1707 | 1771 | 1771
6 | 3F | SL No 540430038696 (EB Unit) | 31779 | 32033 | 32273 | 32474 | 32689 | 32877 | 33011 | 33102 | 33298 | 33528 | 33715 | 33928 | 34105 | 34202 | 34333 | 34545 | 34755 | 34942 | 35183 | 35363 | 35501 | 35615 | 35851 | 36029 | 36243 | 36441 | 36639 | 36745 | 36895 | 37080 | 37226 | 37338
|  | DG | 1999 | 2043 | 2043 | 2043 | 2043 | 2050 | 2062 | 2066 | 2103 | 2103 | 2156 | 2171 | 2218 | 2239 | 2239 | 2256 | 2289 | 2321 | 2321 | 2343 | 2354 | 2354 | 2354 | 2366 | 2366 | 2376 | 2376 | 2376 | 2376 | 2428 | 2510 | 2510
7 | 3F | SL No 540430038843 (EB Unit) | 109964 | 110764 | 111416 | 112077 | 112739 | 113317 | 113782 | 114082 | 114644 | 115361 | 115951 | 116562 | 117123 | 117600 | 117970 | 118563 | 119149 | 119733 | 120427 | 121003 | 121482 | 121925 | 122610 | 123242 | 123975 | 124630 | 125296 | 125863 | 126392 | 126986 | 127494 | 127802
|  | DG | 5120 | 5217 | 5217 | 5217 | 5217 | 5236 | 5288 | 5300 | 5380 | 5380 | 5525 | 5561 | 5662 | 5796 | 5796 | 5845 | 5951 | 6051 | 6051 | 6109 | 6152 | 6152 | 6152 | 6186 | 6186 | 6213 | 6213 | 6216 | 6216 | 6344 | 6554 | 6554
8 | 3F | SL No 540430038848 (EB Unit) | 23959 | 24164 | 24290 | 24433 | 24558 | 24681 | 24790 | 24929 | 25036 | 25164 | 25257 | 25372 | 25460 | 25564 | 25675 | 25800 | 25883 | 26009 | 26114 | 26232 | 26332 | 26448 | 26583 | 26736 | 26866 | 26984 | 27102 | 27231 | 27310 | 27428 | 27512 | 27550
|  | DG | 969 | 987 | 987 | 987 | 987 | 991 | 1009 | 1024 | 1036 | 1036 | 1056 | 1063 | 1080 | 1135 | 1135 | 1141 | 1168 | 1184 | 1184 | 1187 | 1192 | 1192 | 1192 | 1197 | 1197 | 1201 | 1201 | 1201 | 1201 | 1222 | 1261 | 1261
1 | 3F | AHU1 | 10907 | 10960 | 11053 | 11138 | 11205 | 11270 | 11311 | 11311 | 11406 | 11516 | 11588 | 11678 | 11757 | 11797 | 11797 | 11883 | 11973 | 12059 | 12180 | 12289 | 12344 | 12344 | 12476 | 12591 | 12706 | 12812 | 12926 | 12977 | 12977 | 13063 | 13118 | 13170
|  | DG | 895 | 895 | 895 | 895 | 895 | 895 | 895 | 895 | 913 | 913 | 943 | 951 | 967 | 982 | 982 | 991 | 1016 | 1039 | 1039 | 1052 | 1066 | 1066 | 1066 | 1074 | 1074 | 1080 | 1080 | 1080 | 1080 | 1109 | 1153 | 1153
2 | 3F | AHU2 | 10321 | 10416 | 10520 | 10618 | 10712 | 10798 | 10855 | 10855 | 10959 | 11068 | 11142 | 11234 | 11291 | 11312 | 11312 | 11405 | 11462 | 11545 | 11619 | 11687 | 11714 | 11714 | 11846 | 11930 | 12004 | 12070 | 12149 | 12187 | 12187 | 12266 | 12323 | 12367
|  | DG | 903 | 926 | 926 | 926 | 926 | 930 | 930 | 930 | 950 | 950 | 988 | 996 | 1010 | 1019 | 1019 | 1030 | 1052 | 1075 | 1075 | 1083 | 1092 | 1092 | 1092 | 1097 | 1097 | 1101 | 1101 | 1101 | 1101 | 1128 | 1175 | 1175
3 | 3F | AHU3 | 8764 | 8862 | 8985 | 9103 | 9219 | 9321 | 9389 | 9389 | 9494 | 9612 | 9689 | 9791 | 9887 | 9930 | 9930 | 10039 | 10124 | 10210 | 10332 | 10444 | 10489 | 10489 | 10624 | 10741 | 10862 | 10973 | 11089 | 11149 | 11149 | 11238 | 11296 | 11346
|  | DG | 923 | 946 | 946 | 946 | 946 | 951 | 951 | 951 | 970 | 970 | 993 | 1002 | 1021 | 1039 | 1039 | 1050 | 1075 | 1098 | 1098 | 1112 | 1126 | 1126 | 1126 | 1134 | 1134 | 1141 | 1141 | 1141 | 1141 | 1171 | 1218 | 1218
4 | 3F | AHU4 | 8579 | 8687 | 8796 | 8898 | 9002 | 9094 | 9161 | 9161 | 9254 | 9359 | 9432 | 9523 | 9605 | 9641 | 9641 | 9738 | 9825 | 9908 | 10022 | 10126 | 10168 | 10168 | 10305 | 10412 | 10519 | 10614 | 10719 | 10778 | 10778 | 10865 | 10920 | 10968
|  | DG | 782 | 782 | 782 | 782 | 782 | 782 | 782 | 782 | 800 | 800 | 831 | 839 | 855 | 870 | 870 | 881 | 905 | 927 | 927 | 939 | 952 | 952 | 952 | 959 | 959 | 965 | 965 | 965 | 965 | 993 | 1038 | 1038
1 | 3F | AHU1 - BTU | 83302.6 | 84492.81 | 85513.26 | 86362.28 | 87014.04 | 87636.97 | 88092.45 | 88092.45 | 89275.93 | 90140.84 | 91071.91 | 91799.95 | 92376.86 | 92727.48 | 92727.48 | 93836.99 | 94902.87 | 95903.87 | 96822.71 | 97676.98 | 98086.94 | 98086.94 | 99242.89 | 100102.18 | 100772.31 | 101510.24 | 102180.17 | 102780.19 | 102780.19 | 103987.75 | 105032.88 | 105491.36
2 | 3F | AHU2 - BTU | 84127.73 | 85305.72 | 86276.34 | 86980.43 | 87602.88 | 88229.4 | 88611.63 | 88611.63 | 89579.5 | 90300.59 | 90966.53 | 91644.45 | 92346.13 | 92702.58 | 92702.58 | 93840.79 | 95017.02 | 96125.75 | 97180.62 | 98288.49 | 98831.3 | 98831.3 | 99912.99 | 100776.4 | 101417.81 | 102127.1 | 102814.43 | 103407.45 | 103407.45 | 104749.8 | 105990.3 | 106652.85
3 | 3F | AHU3 - BTU | 87129.6 | 88682.99 | 90084.28 | 91225.43 | 92233.48 | 92972.06 | 93375.03 | 93375.03 | 94552.08 | 95527 | 96364.35 | 97159.45 | 97989.09 | 98468.28 | 98468.28 | 99710.67 | 100924.95 | 101985.66 | 103070.78 | 104231.5 | 104721.24 | 104721.24 | 106078.15 | 107218.94 | 108099.17 | 109098.62 | 109972.01 | 110690.71 | 110690.71 | 111928.79 | 113016.93 | 113637.95
4 | 3F | AHU4 - BTU | 103444.13 | 105005.48 | 106194 | 107109.01 | 107938.18 | 108949.38 | 109519.11 | 109519.11 | 110842.3 | 111768.06 | 112732.5 | 113902.85 | 114846.4 | 115336.17 | 115336.17 | 116789.55 | 118073.23 | 119179.1 | 120123.97 | 121035.88 | 121447.42 | 121447.42 | 122863.19 | 124003.25 | 124903.96 | 125819.93 | 126755.64 | 127503.13 | 127503.13 | 128925.27 | 130141.18 | 130737.1
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
|  | Total Power - EB Unit | [33 empty] | EB
|  | Total Power- DG | [33 empty] | AHU
|  | Total Power Cumulative | [33 empty] | BTU
DG
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3
DG
4 | 3F | AHU4
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## August 24
August 2024
Sr.No | Location | Meter | Previous Reading | 2024-08-01 | 2024-08-02 | 2024-08-03 | 2024-08-04 | 2024-08-05 | 2024-08-06 | 2024-08-07 | 2024-08-08 | 2024-08-09 | 2024-08-10 | 2024-08-11 | 2024-08-12 | 2024-08-13 | 2024-08-14 | 2024-08-15 | 2024-08-16 | 2024-08-17 | 2024-08-18 | 2024-08-19 | 2024-08-20 | 2024-08-21 | 2024-08-22 | 2024-08-23 | 2024-08-24 | 2024-08-25 | 2024-08-26 | 2024-08-27 | 2024-08-28 | 2024-08-29 | 2024-08-30 | 2024-08-31 | Consumption
|  |  |  | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 41074 | 41292 | 41545 | 41745 | 41958 | 42213 | 42455 | 42726 | 42987 | 43247 | 43388 | 43608 | 43857 | 44134 | 44350 | 44572 | 44798 | 45018 | 45239 | 45475 | 45714 | 45930 | 46195 | 46460 | 46675 | 46884 | 47000 | 47266 | 47531 | 47790 | 48054 | 48175
|  | DG | 2322 | 2496 | 2496 | 2507 | 2510 | 2510 | 2537 | 2537 | 2537 | 2537 | 2553 | 2553 | 2553 | 2553 | 2627 | 2627 | 2627 | 2627 | 2627 | 2627 | 2646 | 2677 | 2677 | 2677 | 2677 | 2680 | 2836 | 2836 | 2836 | 2836 | 2836 | 2836
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 63982 | 64304 | 64662 | 64937 | 65202 | 65567 | 65911 | 66298 | 66669 | 67003 | 67211 | 67499 | 67852 | 68253 | 68559 | 68848 | 69160 | 69449 | 69739 | 70055 | 70397 | 70708 | 71088 | 71457 | 71751 | 72031 | 72143 | 72563 | 72953 | 73330 | 73700 | 73860
|  | DG | 3540 | 3782 | 3782 | 3791 | 3801 | 3801 | 3845 | 3845 | 3845 | 3845 | 3918 | 3918 | 3918 | 3918 | 3971 | 3971 | 3971 | 3971 | 3971 | 3971 | 3996 | 4045 | 4045 | 4045 | 4045 | 4048 | 4287 | 4287 | 4287 | 4287 | 4287 | 4287
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 25219 | 25390 | 25572 | 25672 | 25772 | 25965 | 26141 | 26340 | 26534 | 26716 | 26799 | 26922 | 27180 | 27319 | 27472 | 27576 | 27745 | 27845 | 27949 | 28106 | 28297 | 28458 | 28637 | 28817 | 28922 | 29025 | 29089 | 29290 | 29498 | 29699 | 29895 | 29957
|  | DG | 1771 | 1882 | 1882 | 1885 | 1888 | 1888 | 1910 | 1910 | 1910 | 1910 | 1944 | 1944 | 1944 | 1944 | 1971 | 1971 | 1971 | 1971 | 1971 | 1971 | 1982 | 2012 | 2012 | 2012 | 2012 | 2014 | 2151 | 2151 | 2151 | 2151 | 2151 | 2151
6 | 3F | SL No 540430038646 (EB Unit) | 37338 | 37540 | 37743 | 37847 | 37945 | 38158 | 38386 | 38620 | 38835 | 39036 | 39099 | 39191 | 39377 | 39601 | 39768 | 39866 | 40049 | 40185 | 40310 | 40531 | 40742 | 40915 | 41138 | 41366 | 41483 | 41611 | 41663 | 41884 | 42089 | 42301 | 42507 | 42580
|  | DG | 2510 | 2624 | 2624 | 2625 | 2633 | 2633 | 2665 | 2665 | 2665 | 2665 | 2700 | 2700 | 2700 | 2700 | 2730 | 2730 | 2730 | 2730 | 2730 | 2730 | 2734 | 2767 | 2767 | 2767 | 2767 | 2768 | 2930 | 2930 | 2930 | 2930 | 2930 | 2930
7 | 3F | SL No 540430038843 (EB Unit) | 127802 | 128427 | 129091 | 129579 | 130035 | 130676 | 131286 | 132012 | 132712 | 133384 | 133764 | 134284 | 134875 | 135663 | 136252 | 136421 | 136974 | 137523 | 138070 | 138736 | 139410 | 139972 | 140644 | 141324 | 141882 | 142364 | 142601 | 143300 | 143982 | 144684 | 145419 | 145691
|  | DG | 6554 | 7051 | 7051 | 7075 | 7091 | 7091 | 7155 | 7155 | 7155 | 7155 | 7336 | 7336 | 7336 | 7336 | 7421 | 7421 | 7421 | 7421 | 7421 | 7421 | 7452 | 7534 | 7534 | 7534 | 7534 | 7543 | 7987 | 7987 | 7987 | 7987 | 7987 | 7987
8 | 3F | SL No 540430038848 (EB Unit) | 27550 | 27652 | 27772 | 27908 | 28025 | 28167 | 28236 | 28370 | 28532 | 28691 | 28820 | 28985 | 29164 | 29312 | 29455 | 29585 | 29759 | 29873 | 30035 | 30187 | 30335 | 30455 | 30619 | 30744 | 30901 | 31015 | 31118 | 31261 | 31452 | 31590 | 31792 | 31846
|  | DG | 1261 | 1360 | 1360 | 1366 | 1368 | 1368 | 1376 | 1376 | 1376 | 1376 | 1433 | 1433 | 1433 | 1433 | 1456 | 1456 | 1456 | 1456 | 1456 | 1456 | 1479 | 1489 | 1489 | 1489 | 1489 | 1491 | 1584 | 1584 | 1584 | 1584 | 1584 | 1584
1 | 3F | AHU1 | 13170 | 13266 | 13367 | 13418 | 13418 | 13532 | 13630 | 13734 | 13836 | 13933 | 13951 | 13951 | 14051 | 14146 | 14216 | 14216 | 14301 | 14350 | 14350 | 14433 | 14526 | 14595 | 14684 | 14770 | 14817 | 14817 | 14827 | 14920 | 15015 | 15110 | 15208 | 15229
|  | DG | 1153 | 1206 | 1206 | 1212 | 1212 | 1212 | 1225 | 1225 | 1225 | 1225 | 1264 | 1264 | 1264 | 1264 | 1282 | 1282 | 1282 | 1282 | 1282 | 1282 | 1282 | 1297 | 1297 | 1297 | 1297 | 1297 | 1394 | 1394 | 1394 | 1394 | 1394 | 1394
2 | 3F | AHU2 | 12367 | 12430 | 12507 | 12531 | 12531 | 12601 | 12662 | 12725 | 12788 | 12850 | 12863 | 12863 | 12936 | 13001 | 13050 | 13050 | 13107 | 13140 | 13140 | 13223 | 13316 | 13391 | 13480 | 13561 | 13595 | 13595 | 13605 | 13708 | 13812 | 13913 | 14015 | 14037
|  | DG | 1175 | 1211 | 1211 | 1214 | 1214 | 1214 | 1222 | 1222 | 1222 | 1222 | 1247 | 1247 | 1247 | 1247 | 1258 | 1258 | 1258 | 1258 | 1258 | 1258 | 1258 | 1275 | 1275 | 1275 | 1275 | 1275 | 1377 | 1377 | 1377 | 1377 | 1377 | 1377
3 | 3F | AHU3 | 11346 | 11456 | 11539 | 11616 | 11616 | 11732 | 11834 | 11942 | 12052 | 12164 | 12185 | 12185 | 12300 | 12407 | 12495 | 12495 | 12604 | 12669 | 12669 | 12759 | 12853 | 12928 | 13026 | 13122 | 13157 | 13157 | 13167 | 13264 | 13358 | 13455 | 13559 | 13582
|  | DG | 1218 | 1279 | 1279 | 1285 | 1285 | 1285 | 1298 | 1298 | 1298 | 1298 | 1341 | 1341 | 1341 | 1341 | 1362 | 1362 | 1362 | 1362 | 1362 | 1362 | 1362 | 1378 | 1378 | 1378 | 1378 | 1378 | 1472 | 1472 | 1472 | 1472 | 1472 | 1472
4 | 3F | AHU4 | 10968 | 11069 | 11171 | 11223 | 11223 | 11334 | 11430 | 11535 | 11637 | 11736 | 11755 | 11755 | 11859 | 11960 | 12040 | 12040 | 12147 | 12202 | 12202 | 12287 | 12387 | 12467 | 12564 | 12661 | 12711 | 12711 | 12718 | 12833 | 12914 | 12958 | 13007 | 13023
|  | DG | 1038 | 1096 | 1096 | 1102 | 1102 | 1102 | 1118 | 1118 | 1118 | 1118 | 1157 | 1157 | 1157 | 1157 | 1175 | 1175 | 1175 | 1175 | 1175 | 1175 | 1175 | 1192 | 1192 | 1192 | 1192 | 1192 | 1287 | 1287 | 1287 | 1287 | 1287 | 1287
1 | 3F | AHU1 - BTU | 105491.36 | 106681.66 | 107328.37 | 107774.45 | 107774.45 | 108807.72 | 109643.75 | 110409.85 | 111051.93 | 111705.25 | 112033.31 | 112033.31 | 113020.91 | 114019.42 | 114932.74 | 114932.74 | 115860.72 | 116271.87 | 116271.87 | 117228.87 | 118297.95 | 119087.81 | 119872.3 | 120483.17 | 120915.77 | 120915.77 | 122207.02 | 123312.55 | 124219.4 | 124794.27 | 125476.67 | 125611
2 | 3F | AHU2 - BTU | 106652.85 | 108172.67 | 109044.47 | 109623.23 | 109623.23 | 110705.24 | 111558.07 | 112478.65 | 113126.42 | 113851.7 | 114346.31 | 114346.31 | 115248.36 | 116117.64 | 116928.92 | 116928.92 | 118010.57 | 118622.32 | 118622.32 | 119779.91 | 120997.48 | 122224.54 | 123253.37 | 124618.44 | 125477.95 | 125477.95 | 125691.09 | 126529.22 | 127454.33 | 128290.49 | 129289.71 | 129491
3 | 3F | AHU3 - BTU | 113637.95 | 115077.08 | 115934.9 | 116414.63 | 116414.63 | 117562.07 | 118517.4 | 119492.19 | 120335.4 | 121135.42 | 121669.78 | 121669.78 | 122678.96 | 123637.49 | 124450.24 | 124450.24 | 125384.11 | 125869.23 | 125869.23 | 126955.12 | 128117.06 | 129126.9 | 129977.56 | 130794.35 | 131206.81 | 131206.81 | 132399.57 | 133468.99 | 134564.2 | 135502.54 | 136412.24 | 136638
4 | 3F | AHU4 - BTU | 130737.1 | 132032.14 | 132902.89 | 133355.68 | 133355.68 | 134790.24 | 135822.31 | 136733.19 | 137604.6 | 138436.45 | 138949.33 | 138949.33 | 140202.45 | 141236.04 | 142125.01 | 142125.01 | 143166.62 | 143517.28 | 143517.28 | 144693.45 | 145910.46 | 146900.61 | 147911.42 | 148890.74 | 149419.9 | 149419.9 | 150780.46 | 151765.21 | 152990.8 | 153819.54 | 154837.29 | 155000
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
|  | DG | [33 empty] | EB
7 | 3F | SL No 540430038843 (EB Unit) | [33 empty] | AHU
|  | DG | [33 empty] | BTU
8 | 3F | SL No 540430038848 (EB Unit) | [33 empty] | DG
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3
DG
4 | 3F | AHU4
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## September 24
September 2024
Sr.No | Location | Meter | Previous Reading | 2024-09-01 | 2024-09-02 | 2024-09-03 | 2024-09-04 | 2024-09-05 | 2024-09-06 | 2024-09-07 | 2024-09-08 | 2024-09-09 | 2024-09-10 | 2024-09-11 | 2024-09-12 | 2024-09-13 | 2024-09-14 | 2024-09-15 | 2024-09-16 | 2024-09-17 | 2024-09-18 | 2024-09-19 | 2024-09-20 | 2024-09-21 | 2024-09-22 | 2024-09-23 | 2024-09-24 | 2024-09-25 | 2024-09-26 | 2024-09-27 | 2024-09-28 | 2024-09-29 | 2024-09-30 | Consumption
|  |  |  | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 48175 | 48505 | 48730 | 48941 | 49158 | 49424 | 49652 | 49880 | 50103 | 50366 | 50607 | 50838 | 51097 | 51289 | 51489 | 51705 | 51968 | 52229 | 52492 | 52750 | 53005 | 53216 | 53426 | 53606 | 53799 | 54074 | 54248 | 54282 | 54484 | 54690 | 54816
|  | DG | 2836 | 2836 | 2881 | 2954 | 2999 | 2999 | 2999 | 2999 | 2999 | 2999 | 3020 | 3047 | 3054 | 3117 | 3117 | 3117 | 3117 | 3117 | 3117 | 3117 | 3117 | 3117 | 3117 | 3203 | 3217 | 3276 | 3357 | 3571 | 3571 | 3578 | 3578
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 73860 | 74300 | 74623 | 74921 | 75233 | 75614 | 75928 | 76238 | 76531 | 76911 | 77256 | 77586 | 77954 | 78218 | 78483 | 78768 | 79146 | 79519 | 79895 | 80265 | 80626 | 80901 | 81175 | 81421 | 81691 | 82088 | 82333 | 82378 | 82678 | 82910 | 83064
|  | DG | 4287 | 4287 | 4359 | 4475 | 4541 | 4541 | 4541 | 4541 | 4541 | 4541 | 4575 | 4617 | 4626 | 4717 | 4717 | 4717 | 4717 | 4717 | 4717 | 4717 | 4717 | 4717 | 4717 | 4853 | 4958 | 4964 | 5086 | 5387 | 5387 | 5395 | 5395
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 29957 | 30123 | 30302 | 30436 | 30592 | 30793 | 30965 | 31071 | 31177 | 31366 | 31545 | 31709 | 31910 | 32050 | 32153 | 32258 | 32466 | 32668 | 32861 | 33057 | 33248 | 33351 | 33461 | 33595 | 33738 | 33943 | 34068 | 34088 | 34213 | 34330 | 34422
|  | DG | 2151 | 2151 | 2190 | 2241 | 2281 | 2281 | 2281 | 2281 | 2281 | 2281 | 2295 | 2317 | 2321 | 2369 | 2369 | 2369 | 2369 | 2369 | 2369 | 2369 | 2369 | 2369 | 2369 | 2446 | 2508 | 2511 | 2582 | 2747 | 2747 | 2751 | 2751
6 | 3F | SL No 540430038646 (EB Unit) | 42580 | 42724 | 42926 | 43086 | 43286 | 43496 | 43701 | 43833 | 43955 | 44197 | 44392 | 44579 | 44782 | 44923 | 45012 | 45124 | 45343 | 45571 | 45785 | 46014 | 46211 | 46331 | 46443 | 46596 | 46748 | 47010 | 47157 | 47173 | 47272 | 47384 | 47463
|  | DG | 2930 | 2930 | 2972 | 3027 | 3072 | 3072 | 3072 | 3072 | 3072 | 3072 | 3093 | 3126 | 3129 | 3185 | 3185 | 3185 | 3185 | 3185 | 3185 | 3185 | 3185 | 3185 | 3185 | 3285 | 3326 | 3364 | 3454 | 3661 | 3661 | 3663 | 3663
7 | 3F | SL No 540430038843 (EB Unit) | 145691 | 146683 | 147335 | 147965 | 148490 | 149183 | 149830 | 150432 | 150891 | 151614 | 152256 | 152879 | 153572 | 154141 | 154584 | 154925 | 155591 | 156230 | 156896 | 157576 | 158236 | 158666 | 159019 | 159471 | 159967 | 160659 | 161087 | 161182 | 161595 | 161927 | 162234
|  | DG | 7987 | 7987 | 8100 | 8282 | 8426 | 8426 | 8426 | 8426 | 8426 | 8426 | 8479 | 8552 | 8577 | 8717 | 8717 | 8717 | 8717 | 8717 | 8717 | 8717 | 8717 | 8717 | 8717 | 8940 | 9121 | 9137 | 9372 | 9929 | 9929 | 9950 | 9950
8 | 3F | SL No 540430038848 (EB Unit) | 31846 | 32184 | 32334 | 32509 | 32592 | 32733 | 32873 | 32992 | 33136 | 33267 | 33409 | 33536 | 33710 | 33831 | 33963 | 34094 | 34255 | 34381 | 34540 | 34654 | 34814 | 34934 | 35090 | 35196 | 35337 | 35445 | 35559 | 35594 | 35738 | 35851 | 35970
|  | DG | 1584 | 1584 | 1609 | 1651 | 1661 | 1661 | 1661 | 1661 | 1661 | 1661 | 1674 | 1684 | 1686 | 1707 | 1707 | 1707 | 1707 | 1707 | 1707 | 1707 | 1707 | 1707 | 1707 | 1740 | 1761 | 1765 | 1783 | 1882 | 1882 | 1887 | 1887
1 | 3F | AHU1 | 15229 | 15284 | 15385 | 15470 | 15470 | 15638 | 15745 | 15828 | 15828 | 15932 | 16013 | 16088 | 16171 | 16233 | 16299 | 16299 | 16390 | 16469 | 16553 | 16647 | 16745 | 16801 | 16801 | 16855 | 16909 | 17008 | 17053 | 17053 | 17115 | 17115 | 17175
|  | DG | 1394 | 1394 | 1420 | 1467 | 1498 | 1498 | 1498 | 1498 | 1498 | 1498 | 1510 | 1523 | 1523 | 1546 | 1546 | 1546 | 1546 | 1546 | 1546 | 1546 | 1546 | 1546 | 1546 | 1597 | 1638 | 1639 | 1686 | 1779 | 1779 | 1779 | 1779
2 | 3F | AHU2 | 14037 | 14104 | 14214 | 14294 | 14362 | 14462 | 14564 | 14645 | 14646 | 14753 | 14829 | 14900 | 14987 | 15061 | 15107 | 15107 | 15208 | 15316 | 15402 | 15492 | 15585 | 15628 | 15628 | 15690 | 15742 | 15840 | 15884 | 15884 | 15957 | 15957 | 16020
|  | DG | 1377 | 1377 | 1404 | 1445 | 1476 | 1476 | 1476 | 1476 | 1476 | 1476 | 1484 | 1497 | 1497 | 1518 | 1518 | 1518 | 1518 | 1518 | 1518 | 1518 | 1518 | 1518 | 1518 | 1564 | 1606 | 1610 | 1655 | 1735 | 1735 | 1735 | 1735
3 | 3F | AHU3 | 13582 | 13637 | 13738 | 13811 | 13883 | 13974 | 14068 | 14144 | 14144 | 14243 | 14333 | 14413 | 14505 | 14576 | 14625 | 14625 | 14694 | 14820 | 14913 | 15001 | 15094 | 15144 | 15144 | 15196 | 15247 | 15350 | 15393 | 15393 | 15465 | 15465 | 15531
|  | DG | 1472 | 1472 | 1496 | 1534 | 1566 | 1566 | 1566 | 1566 | 1566 | 1566 | 1578 | 1593 | 1593 | 1615 | 1615 | 1615 | 1615 | 1615 | 1615 | 1615 | 1615 | 1615 | 1615 | 1663 | 1704 | 1704 | 1751 | 1826 | 1826 | 1826 | 1826
4 | 3F | AHU4 | 13023 | 13049 | 13149 | 13223 | 13289 | 13378 | 13461 | 13545 | 13546 | 13642 | 13713 | 13796 | 13884 | 13949 | 14017 | 14017 | 14103 | 14192 | 14274 | 14353 | 14436 | 14483 | 14483 | 14528 | 14578 | 14666 | 14707 | 14707 | 14776 | 14776 | 14836
|  | DG | 1287 | 1287 | 1307 | 1345 | 1374 | 1374 | 1374 | 1374 | 1374 | 1374 | 1382 | 1399 | 1399 | 1421 | 1421 | 1421 | 1421 | 1421 | 1421 | 1421 | 1421 | 1421 | 1421 | 1461 | 1494 | 1495 | 1539 | 1637 | 1637 | 1637 | 1637
1 | 3F | AHU1 - BTU | 125611 | 126471.66 | 127754.19 | 129122.9 | 129709.71 | 130224.85 | 130635 | 131044.39 | 131044.39 | 132026.45 | 132742.04 | 133382.29 | 133937 | 134411.74 | 134671.54 | 134671.54 | 135657.67 | 136371.57 | 137076 | 137671.9 | 138290.86 | 138573.36 | 138573.36 | 139677.43 | 140629.32 | 141348.66 | 142078.1 | 142800 | 143217 | 143217 | 144022
2 | 3F | AHU2 - BTU | 129491 | 130355.97 | 131676.42 | 133022.7 | 133836.77 | 134714.57 | 135559.49 | 136281.36 | 136281.36 | 137423.44 | 138363.48 | 139122.62 | 139817.36 | 140285.49 | 140883.1 | 140883.1 | 141898.31 | 142727.09 | 143345.65 | 144143.17 | 144878.86 | 145360.85 | 145360.85 | 146563.58 | 147606.7 | 148697.44 | 149650 | 150488 | 151292 | 151292 | 152135
3 | 3F | AHU3 - BTU | 136638 | 137390.83 | 138727.26 | 139995.68 | 140801.53 | 141552.19 | 142280.01 | 142962.73 | 142962.73 | 144162.84 | 145116.13 | 145963.67 | 146772.08 | 147515.64 | 148090.03 | 148090.03 | 149078.09 | 149895.74 | 150653.02 | 151456.63 | 152262.66 | 152631.66 | 152631.66 | 153722.11 | 154787.1 | 155703.13 | 156625.1 | 157471 | 158134 | 158134 | 158977
4 | 3F | AHU4 - BTU | 155000 | 155795.12 | 157212.97 | 158688.59 | 159546.78 | 160293.8 | 160982.11 | 161569.39 | 161569.39 | 162934.99 | 163953.28 | 164844.37 | 165688.03 | 166343.24 | 166732.37 | 166732.37 | 167769.8 | 168562.83 | 169302.76 | 170110.65 | 170875.49 | 171200.27 | 171200.27 | 172410.61 | 173441.05 | 174318.53 | 175487.87 | 176384 | 176899 | 176899 | 177713
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [31 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit) | [32 empty] | EB
|  | DG | [32 empty] | AHU
7 | 3F | SL No 540430038843 (EB Unit) | [32 empty] | BTU
|  | DG | [32 empty] | DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3
DG
4 | 3F | AHU4
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## Oct 24
October 2024
Sr.No | Location | Meter | Previous Reading | 2024-10-01 | 2024-10-02 | 2024-10-03 | 2024-10-04 | 2024-10-05 | 2024-10-06 | 2024-10-07 | 2024-10-08 | 2024-10-09 | 2024-10-10 | 2024-10-11 | 2024-10-12 | 2024-10-13 | 2024-10-14 | 2024-10-15 | 2024-10-16 | 2024-10-17 | 2024-10-18 | 2024-10-19 | 2024-10-20 | 2024-10-21 | 2024-10-22 | 2024-10-23 | 2024-10-24 | 2024-10-25 | 2024-10-26 | 2024-10-27 | 2024-10-28 | 2024-10-29 | 2024-10-30 | 2024-10-31 | Consumption
|  |  |  | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 54816 | 55183 | 55389 | 55661 | 55913 | 56117 | 56319 | 56597 | 56862 | 57081 | 57327 | 57583 | 57795 | 58004 | 58270 | 58557 | 58807 | 59081 | 59318 | 59521 | 59731 | 60021 | 60266 | 60534 | 60798 | 61043 | 61254 | 61469 | 61709 | 61953 | 62161 | 62276
|  | DG | 3578 | 3626 | 3630 | 3630 | 3630 | 3630 | 3630 | 3630 | 3631 | 3663 | 3663 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3665 | 3678 | 3678 | 3678 | 3678 | 3678 | 3678 | 3678 | 3678 | 3678 | 3678 | 3678 | 3678 | 3678 | 3678
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 83064 | 83574 | 83846 | 84233 | 84587 | 84854 | 85127 | 85517 | 85896 | 86225 | 86592 | 86919 | 87197 | 87471 | 87844 | 88255 | 88627 | 89017 | 89356 | 89622 | 89877 | 90313 | 90670 | 91053 | 91431 | 91774 | 92050 | 92332 | 92667 | 93000 | 93280 | 93430
|  | DG | 5395 | 5468 | 5474 | 5474 | 5474 | 5474 | 5474 | 5474 | 5476 | 5517 | 5517 | 5519 | 5519 | 5519 | 5519 | 5519 | 5519 | 5519 | 5538 | 5538 | 5538 | 5538 | 5538 | 5538 | 5538 | 5538 | 5538 | 5538 | 5538 | 5538 | 5538 | 5538
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 34422 | 34691 | 34790 | 34985 | 35169 | 35267 | 35377 | 35596 | 35802 | 35990 | 36187 | 36335 | 36453 | 36561 | 36785 | 37020 | 37228 | 37441 | 37634 | 37731 | 37834 | 38063 | 38259 | 38475 | 38680 | 38872 | 38991 | 39112 | 39307 | 39491 | 39608 | 39703
|  | DG | 2751 | 2790 | 2792 | 2792 | 2792 | 2792 | 2792 | 2792 | 2793 | 2814 | 2814 | 2815 | 2815 | 2815 | 2815 | 2815 | 2815 | 2815 | 2826 | 2826 | 2826 | 2826 | 2826 | 2826 | 2826 | 2826 | 2826 | 2826 | 2826 | 2826 | 2826 | 2826
6 | 3F | SL No 540430038646 (EB Unit) | 47463 | 47762 | 47894 | 48144 | 48376 | 48496 | 48608 | 48853 | 49071 | 49282 | 49480 | 49680 | 49785 | 49898 | 50144 | 50412 | 50653 | 50894 | 51102 | 51201 | 51319 | 51545 | 51761 | 51907 | 52225 | 52456 | 52596 | 52740 | 52976 | 53204 | 53397 | 53462
|  | DG | 3663 | 3694 | 3696 | 3696 | 3696 | 3696 | 3696 | 3696 | 3698 | 3721 | 3721 | 3723 | 3723 | 3723 | 3723 | 3723 | 3723 | 3723 | 3732 | 3732 | 3732 | 3732 | 3732 | 3732 | 3732 | 3732 | 3732 | 3732 | 3732 | 3732 | 3732 | 3732
7 | 3F | SL No 540430038843 (EB Unit) | 162234 | 163299 | 163637 | 164268 | 164940 | 165419 | 165683 | 166345 | 166980 | 167553 | 168192 | 168822 | 169242 | 169505 | 170408 | 171106 | 171801 | 172532 | 173162 | 173540 | 174122 | 174826 | 175475 | 176173 | 176892 | 177515 | 177923 | 178381 | 179046 | 179757 | 180328 | 180492
|  | DG | 9950 | 10045 | 10054 | 10054 | 10054 | 10054 | 10054 | 10054 | 10060 | 10100 | 10100 | 10104 | 10104 | 10104 | 10104 | 10104 | 10104 | 10104 | 10150 | 10150 | 10150 | 10150 | 10150 | 10150 | 10150 | 10150 | 10150 | 10150 | 10150 | 10150 | 10150 | 10150
8 | 3F | SL No 540430038848 (EB Unit) | 35970 | 36232 | 36292 | 36444 | 36607 | 36742 | 36914 | 37059 | 37234 | 37328 | 37509 | 37650 | 37791 | 37917 | 38012 | 38082 | 38185 | 38295 | 38424 | 38551 | 38669 | 38858 | 38994 | 39157 | 39247 | 39319 | 39386 | 39453 | 39533 | 39613 | 39686 | 39721
|  | DG | 1887 | 1925 | 1927 | 1927 | 1927 | 1927 | 1927 | 1927 | 1927 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1933 | 1945 | 1945 | 1945 | 1945 | 1945 | 1945 | 1945 | 1945 | 1945 | 1945 | 1945 | 1945 | 1945 | 1945
1 | 3F | AHU1 | 17175 | 17313 | 17315 | 17410 | 17499 | 17499 | 17499 | 17598 | 17682 | 17771 | 17850 | 17932 | 17932 | 17932 | 18022 | 18098 | 18183 | 18266 | 18335 | 18383 | 18383 | 18469 | 18557 | 18650 | 18731 | 18819 | 18875 | 18875 | 18952 | 19026 | 19096 | 19096
|  | DG | 1779 | 1792 | 1792 | 1792 | 1792 | 1792 | 1792 | 1792 | 1793 | 1795 | 1795 | 1796 | 1796 | 1796 | 1796 | 1796 | 1796 | 1796 | 1804 | 1804 | 1804 | 1804 | 1804 | 1804 | 1804 | 1804 | 1804 | 1804 | 1804 | 1804 | 1804 | 1804
2 | 3F | AHU2 | 16020 | 16154 | 16155 | 16256 | 16336 | 16336 | 16336 | 16442 | 16515 | 16598 | 16682 | 16774 | 16774 | 16774 | 16880 | 16978 | 17067 | 17149 | 17233 | 17263 | 17263 | 17361 | 17459 | 17556 | 17649 | 17738 | 17791 | 17791 | 17895 | 17997 | 18091 | 18091
|  | DG | 1735 | 1745 | 1745 | 1745 | 1745 | 1745 | 1745 | 1745 | 1746 | 1748 | 1748 | 1748 | 1748 | 1748 | 1749 | 1749 | 1749 | 1749 | 1758 | 1758 | 1758 | 1758 | 1758 | 1758 | 1758 | 1758 | 1758 | 1758 | 1758 | 1758 | 1758 | 1758
3 | 3F | AHU3 | 15531 | 15678 | 15678 | 15777 | 15865 | 15865 | 15865 | 15963 | 16058 | 16155 | 16248 | 16343 | 16343 | 16343 | 16432 | 16526 | 16631 | 16735 | 16822 | 16856 | 16856 | 16962 | 17067 | 17176 | 17277 | 17375 | 17392 | 17392 | 17475 | 17538 | 17608 | 17608
|  | DG | 1826 | 1840 | 1840 | 1840 | 1840 | 1840 | 1840 | 1840 | 1841 | 1842 | 1842 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1843 | 1854 | 1854 | 1854 | 1854 | 1854 | 1854 | 1854 | 1854 | 1854 | 1854 | 1854 | 1854 | 1854 | 1854
4 | 3F | AHU4 | 14836 | 14970 | 14971 | 15058 | 15145 | 15145 | 15145 | 15237 | 15322 | 15417 | 15505 | 15590 | 15590 | 15590 | 15685 | 15770 | 15859 | 15942 | 16016 | 16066 | 16066 | 16154 | 16238 | 16329 | 16380 | 16444 | 16488 | 16488 | 16555 | 16627 | 16687 | 16687
|  | DG | 1637 | 1649 | 1649 | 1649 | 1649 | 1649 | 1649 | 1649 | 1650 | 1651 | 1651 | 1652 | 1652 | 1652 | 1652 | 1652 | 1652 | 1652 | 1662 | 1662 | 1662 | 1662 | 1662 | 1662 | 1662 | 1662 | 1662 | 1662 | 1662 | 1662 | 1662 | 1662
1 | 3F | AHU1 - BTU | 144022 | 145162 | 145162 | 146079 | 146791 | 146791 | 146791 | 147973 | 148799 | 149410 | 150220 | 150681 | 150681 | 150681 | 151582 | 152340 | 152905 | 153489 | 154078 | 154247 | 154247 | 155098 | 155829 | 156539 | 157223 | 157718 | 157890 | 157890 | 158769 | 159403 | 159746 | 159746
2 | 3F | AHU2 - BTU | 152135 | 153457 | 153457 | 154462 | 155360 | 155360 | 155360 | 156580 | 157655 | 158594 | 159508 | 160104 | 160104 | 160104 | 161197 | 162059 | 162767 | 163447 | 164140 | 164461 | 164461 | 165397 | 166283 | 167091 | 167972 | 168620 | 168942 | 168942 | 169980 | 170712 | 171381 | 171381
3 | 3F | AHU3 - BTU | 158977 | 160207 | 160207 | 161129 | 161902 | 161902 | 161902 | 163111 | 163853 | 164571 | 165358 | 166035 | 166035 | 166035 | 167031 | 167751 | 168516 | 169242 | 169919 | 170287 | 170287 | 171209 | 172020 | 172774 | 173480 | 174061 | 174252 | 174252 | 174996 | 175623 | 176009 | 176009
4 | 3F | AHU4 - BTU | 177713 | 178761 | 178761 | 179823 | 180662 | 180662 | 180662 | 182063 | 183045 | 183857 | 184556 | 185147 | 185147 | 185147 | 186276 | 187028 | 187842 | 188513 | 189110 | 189312 | 189312 | 190291 | 191013 | 191751 | 192384 | 192817 | 192973 | 192973 | 193671 | 194009 | 194290 | 194290
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time |  | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
|  | DG | [33 empty] | EB
6 | 3F | SL No 540430038696 (EB Unit) | [33 empty] | AHU
|  | DG | [33 empty] | BTU
7 | 3F | SL No 540430038843 (EB Unit) | [33 empty] | DG
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3
DG
4 | 3F | AHU4
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## Nov 24
November 2024
Sr.No | Location | Meter | Previous Reading | 2024-11-01 | 2024-11-02 | 2024-11-03 | 2024-11-04 | 2024-11-05 | 2024-11-06 | 2024-11-07 | 2024-11-08 | 2024-11-09 | 2024-11-10 | 2024-11-11 | 2024-11-12 | 2024-11-13 | 2024-11-14 | 2024-11-15 | 2024-11-16 | 2024-11-17 | 2024-11-18 | 2024-11-19 | 2024-11-20 | 2024-11-21 | 2024-11-22 | 2024-11-23 | 2024-11-24 | 2024-11-25 | 2024-11-26 | 2024-11-27 | 2024-11-28 | 2024-11-29 | 2024-11-30 | Consumption
|  |  |  | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 62276 | 62591 | 62802 | 63034 | 63289 | 63523 | 63788 | 64044 | 64300 | 64518 | 64730 | 64968 | 65239 | 65508 | 65746 | 66001 | 66173 | 66383 | 66645 | 66927 | 67179 | 67433 | 67688 | 67894 | 68118 | 68368 | 68628 | 68907 | 69171 | 69415 | 69543
|  | DG | 3678 | 3678 | 3678 | 3678 | 3678 | 3682 | 3682 | 3682 | 3682 | 3684 | 3684 | 3718 | 3718 | 3718 | 3737 | 3737 | 3775 | 3775 | 3775 | 3775 | 3775 | 3775 | 3775 | 3775 | 3775 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 93430 | 93829 | 94127 | 94430 | 94789 | 95105 | 95495 | 95867 | 96230 | 96520 | 96800 | 97145 | 97502 | 97931 | 98268 | 98634 | 98860 | 99135 | 99511 | 99915 | 100274 | 100643 | 100989 | 101274 | 101565 | 101922 | 102295 | 102695 | 103072 | 103421 | 103577
|  | DG | 5538 | 5538 | 5538 | 5538 | 5538 | 5543 | 5543 | 5543 | 5543 | 5547 | 5547 | 5591 | 5591 | 5591 | 5615 | 5615 | 5667 | 5667 | 5667 | 5667 | 5667 | 5667 | 5667 | 5667 | 5667 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 39703 | 39862 | 39901 | 40106 | 40302 | 40476 | 40696 | 40890 | 41078 | 41179 | 41306 | 41492 | 41699 | 41899 | 42073 | 42256 | 42354 | 42459 | 42670 | 42889 | 43089 | 43302 | 43503 | 43626 | 43741 | 43943 | 44162 | 44392 | 44616 | 44820 | 44885
|  | DG | 2826 | 2826 | 2826 | 2826 | 2826 | 2829 | 2829 | 2829 | 2829 | 2831 | 2831 | 2848 | 2848 | 2848 | 2859 | 2859 | 2878 | 2878 | 2878 | 2878 | 2878 | 2878 | 2878 | 2878 | 2878 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886
6 | 3F | SL No 540430038646 (EB Unit) | 53462 | 53637 | 53768 | 53894 | 54130 | 54364 | 54575 | 54840 | 55064 | 55207 | 55307 | 55546 | 55788 | 56022 | 56230 | 56426 | 56512 | 56600 | 56816 | 57025 | 57260 | 57467 | 57690 | 57785 | 57807 | 58110 | 58338 | 58589 | 58813 | 59036 | 59104
|  | DG | 3732 | 3732 | 3732 | 3732 | 3732 | 3735 | 3735 | 3735 | 3735 | 3740 | 3740 | 3757 | 3757 | 3757 | 3766 | 3766 | 3785 | 3785 | 3785 | 3785 | 3785 | 3785 | 3785 | 3785 | 3785 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794
7 | 3F | SL No 540430038843 (EB Unit) | 180492 | 180679 | 181067 | 181462 | 182065 | 182586 | 183366 | 183961 | 184660 | 185152 | 185503 | 186137 | 186836 | 187547 | 188196 | 188899 | 189404 | 189880 | 190523 | 191238 | 191944 | 192607 | 193262 | 193823 | 194191 | 194862 | 195542 | 196247 | 196907 | 197525 | 197767
|  | DG | 10150 | 10150 | 10150 | 10150 | 10150 | 10158 | 10158 | 10158 | 10158 | 10165 | 10165 | 10208 | 10208 | 10208 | 10238 | 10238 | 10292 | 10292 | 10292 | 10292 | 10292 | 10292 | 10292 | 10292 | 10292 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303
8 | 3F | SL No 540430038848 (EB Unit) | 39721 | 39814 | 39886 | 39965 | 40057 | 40129 | 40220 | 40307 | 40386 | 40401 | 40527 | 40593 | 40671 | 40749 | 40865 | 41027 | 41133 | 41280 | 41405 | 41548 | 41624 | 41722 | 41808 | 41919 | 42102 | 42235 | 42401 | 42513 | 42614 | 42662 | 42702
|  | DG | 1945 | 1945 | 1945 | 1945 | 1945 | 1946 | 1946 | 1946 | 1946 | 1948 | 1948 | 1960 | 1960 | 1960 | 1960 | 1960 | 1980 | 1980 | 1980 | 1980 | 1980 | 1980 | 1980 | 1980 | 1980 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983
1 | 3F | AHU1 | 19096 | 19096 | 19161 | 19161 | 19262 | 19352 | 19437 | 19518 | 19594 | 19639 | 19639 | 19732 | 19815 | 19907 | 20002 | 20093 | 20160 | 20160 | 20249 | 20306 | 20362 | 20409 | 20471 | 20528 | 20528 | 20604 | 20683 | 20760 | 20802 | 20853 | 20893
|  | DG | 1804 | 1804 | 1804 | 1804 | 1804 | 1806 | 1806 | 1806 | 1806 | 1808 | 1808 | 1808 | 1808 | 1808 | 1808 | 1808 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811
2 | 3F | AHU2 | 18091 | 18091 | 18143 | 18143 | 18246 | 18337 | 18430 | 18513 | 18589 | 18633 | 18633 | 18723 | 18811 | 18897 | 18985 | 18999 | 19130 | 19130 | 19188 | 19287 | 19345 | 19389 | 19460 | 19516 | 19516 | 19594 | 19677 | 19747 | 19804 | 19864 | 19914
|  | DG | 1758 | 1758 | 1758 | 1758 | 1758 | 1760 | 1760 | 1760 | 1760 | 1762 | 1762 | 1762 | 1762 | 1762 | 1762 | 1762 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764
3 | 3F | AHU3 | 17608 | 17608 | 17662 | 17662 | 17770 | 17862 | 17948 | 18035 | 18177 | 18177 | 18177 | 18284 | 18377 | 18434 | 18535 | 18599 | 18636 | 18636 | 18690 | 18809 | 18894 | 18948 | 19023 | 19094 | 19094 | 19191 | 19285 | 19376 | 19458 | 19546 | 19597
|  | DG | 1854 | 1854 | 1854 | 1854 | 1854 | 1856 | 1856 | 1856 | 1856 | 1856 | 1856 | 1857 | 1857 | 1857 | 1857 | 1857 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858
4 | 3F | AHU4 | 16687 | 16688 | 16731 | 16731 | 16820 | 16899 | 16973 | 17047 | 17118 | 17162 | 17162 | 17240 | 17314 | 17390 | 17477 | 17555 | 17610 | 17610 | 17696 | 17793 | 17891 | 17995 | 18083 | 18163 | 18163 | 18276 | 18395 | 18506 | 18597 | 18689 | 18702
|  | DG | 1662 | 1662 | 1662 | 1662 | 1662 | 1663 | 1663 | 1663 | 1663 | 1666 | 1666 | 1666 | 1666 | 1666 | 1666 | 1666 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668
1 | 3F | AHU1 - BTU | 159746 | 159746 | 159746 | 159746 | 160588 | 161250 | 161983 | 162627 | 163033 | 163234 | 163234 | 164074 | 164717 | 165038 | 165508 | 165863 | 166140 | 166140 | 166851 | 167333 | 167838 | 168357 | 168799 | 169040 | 169040 | 169649 | 170367 | 170936 | 171426 | 171793 | 172072
2 | 3F | AHU2 - BTU | 171381 | 171381 | 171948 | 171948 | 172877 | 173536 | 174280 | 174891 | 175456 | 175708 | 175708 | 176618 | 177263 | 177828 | 178343 | 178824 | 179188 | 179188 | 179839 | 180530 | 181000 | 181503 | 181962 | 182249 | 182249 | 182793 | 183431 | 183944 | 184378 | 184731 | 185120
3 | 3F | AHU3 - BTU | 176009 | 176009 | 176389 | 176389 | 177114 | 177732 | 178387 | 179039 | 179533 | 179760 | 179760 | 180606 | 181230 | 181712 | 182335 | 182782 | 183063 | 183063 | 183713 | 184384 | 184902 | 185365 | 185834 | 186143 | 186143 | 186624 | 187254 | 187744 | 188085 | 188204 | 188463
4 | 3F | AHU4 - BTU | 194290 | 194290 | 194621 | 194621 | 195393 | 195974 | 196583 | 197135 | 197498 | 197681 | 197681 | 198465 | 199030 | 199619 | 200220 | 200783 | 201041 | 201041 | 201645 | 202346 | 202923 | 203318 | 203746 | 203946 | 203946 | 204470 | 205098 | 205698 | 206199 | 206586 | 206669
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [31 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time |  | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
|  | DG | [32 empty] | EB
6 | 3F | SL No 540430038696 (EB Unit) | [32 empty] | AHU
|  | DG | [32 empty] | BTU
7 | 3F | SL No 540430038843 (EB Unit) | [32 empty] | DG
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3
DG
4 | 3F | AHU4
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## DEC - 2024
December 2024
Sr.No | Location | Meter | Previous Reading | 2024-12-01 | 2024-12-02 | 2024-12-03 | 2024-12-04 | 2024-12-05 | 2024-12-06 | 2024-12-07 | 2024-12-08 | 2024-12-09 | 2024-12-10 | 2024-12-11 | 2024-12-12 | 2024-12-13 | 2024-12-14 | 2024-12-15 | 2024-12-16 | 2024-12-17 | 2024-12-18 | 2024-12-19 | 2024-12-20 | 2024-12-21 | 2024-12-22 | 2024-12-23 | 2024-12-24 | 2024-12-25 | 2024-12-26 | 2024-12-27 | 2024-12-28 | 2024-12-29 | 2024-12-30 | 2024-12-31 | Consumption
|  |  |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 69543 | 69870 | 70134 | 70389 | 70653 | 70926 | 71172 | 71394 | 71605 | 71885 | 72143 | 72403 | 72664 | 72900 | 73046 | 73265 | 73528 | 73802 | 74058 | 74309 | 74560 | 74780 | 74984 | 75215 | 75408 | 75736 | 75957 | 76179 | 76387 | 76602 | 76841 | 76944
|  | DG | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3790 | 3793 | 3793 | 3801 | 3801 | 3801 | 3801 | 3801 | 3801 | 3801 | 3801 | 3801
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 103577 | 104024 | 104406 | 104771 | 105155 | 105544 | 105891 | 106186 | 106468 | 106869 | 107241 | 107617 | 107993 | 108345 | 108521 | 108815 | 109201 | 109579 | 109938 | 110301 | 110626 | 110955 | 111228 | 111551 | 111865 | 112114 | 112447 | 112744 | 113018 | 113302 | 113623 | 113760
|  | DG | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5686 | 5691 | 5702 | 5702 | 5702 | 5702 | 5702 | 5702 | 5702 | 5702 | 5702 | 5702
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 44885 | 45068 | 45283 | 45458 | 45700 | 45919 | 46122 | 46240 | 46354 | 46538 | 46724 | 47019 | 47230 | 47430 | 47523 | 47649 | 47868 | 48089 | 48299 | 48496 | 48704 | 48823 | 48942 | 49122 | 49299 | 49435 | 49595 | 49746 | 49852 | 49961 | 50125 | 50207
|  | DG | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2886 | 2888 | 2892 | 2892 | 2892 | 2892 | 2892 | 2892 | 2892 | 2892 | 2892 | 2892
6 | 3F | SL No 540430038646 (EB Unit) | 59104 | 59304 | 59542 | 59766 | 59979 | 60225 | 60452 | 60598 | 60731 | 60996 | 61250 | 61497 | 61703 | 61904 | 61938 | 62027 | 62253 | 62465 | 62680 | 62842 | 63131 | 63229 | 63364 | 63499 | 63729 | 63802 | 63940 | 63940 | 64070 | 64182 | 64265 | 64448
|  | DG | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3794 | 3796 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800
7 | 3F | SL No 540430038843 (EB Unit) | 197767 | 198596 | 199287 | 199981 | 200748 | 201539 | 202275 | 202876 | 203303 | 204066 | 204806 | 205574 | 206358 | 207087 | 207540 | 208041 | 208813 | 209610 | 210355 | 211029 | 211275 | 212639 | 213137 | 213796 | 214462 | 215001 | 215580 | 216082 | 216498 | 216835 | 217378 | 217622
|  | DG | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10303 | 10310 | 10322 | 10322 | 10322 | 10322 | 10322 | 10322 | 10322 | 10322 | 10322 | 10322
8 | 3F | SL No 540430038848 (EB Unit) | 42702 | 42791 | 42862 | 42925 | 43009 | 43081 | 43184 | 43236 | 43292 | 43365 | 43400 | 43515 | 43616 | 43701 | 43768 | 43873 | 43965 | 44067 | 44147 | 44231 | 44311 | 44430 | 44476 | 44572 | 44648 | 44748 | 44829 | 44927 | 45024 | 45155 | 45237 | 45289
|  | DG | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1983 | 1985 | 1985 | 1985 | 1985 | 1985 | 1985 | 1985 | 1985 | 1985 | 1985
1 | 3F | AHU1 | 20893 | 20907 | 20963 | 20989 | 21033 | 21073 | 21110 | 21129 | 21129 | 21206 | 21246 | 21248 | 21322 | 21361 | 21372 | 21372 | 21417 | 21465 | 21500 | 21534 | 21571 | 21576 | 21577 | 21616 | 21650 | 21653 | 21718 | 21760 | 21775 | 21775 | 21814 | 21831
|  | DG | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811
2 | 3F | AHU2 | 19914 | 19927 | 19989 | 20047 | 20106 | 20163 | 20219 | 20248 | 20248 | 20348 | 20411 | 20470 | 20530 | 20592 | 20616 | 20616 | 20682 | 20735 | 20804 | 20858 | 20916 | 20923 | 20923 | 20984 | 21039 | 21108 | 21228 | 21344 | 21379 | 21379 | 21444 | 21457
|  | DG | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1764 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765
3 | 3F | AHU3 | 19597 | 19610 | 19688 | 19760 | 19830 | 19897 | 19979 | 20025 | 20025 | 20106 | 20185 | 20275 | 20363 | 20454 | 20478 | 20478 | 20572 | 20645 | 20749 | 20831 | 20917 | 20928 | 20928 | 21022 | 21107 | 21110 | 21132 | 21145 | 21152 | 21152 | 21190 | 21190
|  | DG | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1858 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859
4 | 3F | AHU4 | 18702 | 18719 | 18786 | 18845 | 18903 | 18963 | 19023 | 19055 | 19055 | 19142 | 19187 | 19230 | 19272 | 19313 | 19324 | 19324 | 19398 | 19486 | 19529 | 19569 | 19611 | 19616 | 19616 | 19661 | 19701 | 19703 | 19708 | 19714 | 19718 | 19718 | 19719 | 19720
|  | DG | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668
1 | 3F | AHU1 - BTU | 172072 | 172072 | 172674 | 173320 | 173860 | 174341 | 174774 | 174825 | 174825 | 175335 | 175740 | 176158 | 176497 | 176810 | 176854 | 176854 | 177368 | 177796 | 178199 | 178518 | 178905 | 178973 | 178973 | 179374 | 179708 | 179708 | 179745 | 179747 | 179748 | 179748 | 180098 | 180287
2 | 3F | AHU2 - BTU | 185120 | 185120 | 185722 | 186431 | 187015 | 187507 | 187910 | 188015 | 188015 | 188548 | 189013 | 189434 | 189809 | 190124 | 190173 | 190173 | 190640 | 191060 | 191392 | 191689 | 192040 | 192083 | 192083 | 192325 | 192610 | 192610 | 192681 | 192691 | 192691 | 192691 | 192828 | 192836
3 | 3F | AHU3 - BTU | 188463 | 188463 | 188929 | 189513 | 190050 | 190541 | 190865 | 190968 | 190968 | 191390 | 191634 | 191751 | 191923 | 192204 | 192228 | 192228 | 192585 | 192843 | 193131 | 193436 | 193815 | 193855 | 193855 | 194070 | 194252 | 194252 | 194256 | 194256 | 194257 | 194257 | 194316 | 194316
4 | 3F | AHU4 - BTU | 206669 | 206669 | 207129 | 207645 | 208062 | 208351 | 208586 | 208649 | 208649 | 209083 | 209364 | 209567 | 209805 | 210065 | 210073 | 210073 | 210447 | 210712 | 210945 | 211145 | 211428 | 211458 | 211458 | 211643 | 211755 | 211755 | 211758 | 211758 | 211758 | 211758 | 211795 | 211795
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time |  | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
|  | DG | [33 empty] | EB
6 | 3F | SL No 540430038696 (EB Unit) | [33 empty] | AHU
|  | DG | [33 empty] | BTU
7 | 3F | SL No 540430038843 (EB Unit) | [33 empty] | DG
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3
DG
4 | 3F | AHU4
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## summary
Sr.No. | Consumption | July'24 | Aug'24 | Sept'24 | Oct'24 | Nov'24 | Dec'24 | Jan'25 | Feb'25 | Mar'25 | Apr'25 | May'25 | Jun'25 | Jul'25 | Aug'25 | Sep'25 | Oct'25 | Nov'25 | Dec'25 | 2026-01-01 | 2026-02-01 | 2026-03-01 | 2026-04-01 | 2026-05-01 | 2026-06-01 | 2026-07-01 | 2026-08-01
1 | EB
2 | AHU
3 | DG
4 | BTU
5 | Total
Sr.No. | Cost | July'24 | Aug'24 | Sept'24 | Oct'24 | Nov'24 | Dec'24 | Jan'25 | Feb'25 | Mar'25 | Apr'25 | May'25 | Jun'25 | Jul'25 | Aug'25 | Sep'25 | Oct'25 | Nov'25 | Dec'25 | 2026-01-01 | 2026-02-01 | 2026-03-01 | 2026-04-01 | 2026-05-01 | 2026-06-01 | 2026-07-01 | 2026-08-01
1 | EB
2 | AHU
3 | DG
4 | BTU
5 | Total
[9 empty] | Jan-26 to june 26 | 3953205 | Saving | 519408
| Jan-25 to june -25 | [6 empty] | 4472613

## July-2026
JULY - 2026
Sr.No | Location | Meter | Previous Reading | 2026-07-01 | 2026-07-02 | 2026-07-03 | 2026-07-04 | 2026-07-05 | 2026-07-06 | 2026-07-07 | 2026-07-08 | 2026-07-09 | 2026-07-10 | 2026-07-11 | 2026-07-12 | 2026-07-13 | 2026-07-14 | 2026-07-15 | 2026-07-16 | 2026-07-17 | 2026-07-18 | 2026-07-19 | 2026-07-20 | 2026-07-21 | 2026-07-22 | 2026-07-23 | 2026-07-24 | 2026-07-25 | 2026-07-26 | 2026-07-27 | 2026-07-28 | 2026-07-29 | 2026-07-30 | 2026-07-31 | Consumption
|  |  |  | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 210307 | 210554 | 210800 | 211054 | 211245 | 211447 | 211710 | 211951 | 212208 | 212453 | 212678 | 212890 | 213089 | 213341 | 213595 | 213844 | 214099 | 214346 | 214550 | 214746 | 214991 | 215245 | 215310 | 215762 | 215959 | 216204 | 216400 | 216663 | 216907 | 217151 | 217410 | 217557
|  | DG | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 303867 | 304225 | 304577 | 304934 | 305189 | 305452 | 305826 | 306176 | 306539 | 306885 | 307205 | 307484 | 307743 | 308105 | 308467 | 308830 | 309196 | 309540 | 309816 | 310071 | 310418 | 310784 | 311167 | 311529 | 311864 | 312133 | 312389 | 312762 | 313109 | 313457 | 313830 | 314041
|  | DG | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 160838 | 161040 | 161246 | 161453 | 161591 | 161720 | 161940 | 162137 | 162342 | 162539 | 162725 | 162874 | 163000 | 163202 | 163405 | 163616 | 163823 | 164025 | 164153 | 164260 | 164468 | 164682 | 164682 | 165121 | 165322 | 165471 | 165600 | 165829 | 166037 | 166254 | 166475 | 166606
|  | DG | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459
6 | 3F | SL No 540430038646 (EB Unit) | 179845 | 180108 | 180355 | 180610 | 180732 | 180853 | 181122 | 181389 | 181656 | 181902 | 182148 | 182302 | 182423 | 182697 | 182975 | 183255 | 183520 | 183771 | 183905 | 184030 | 184297 | 184573 | 184850 | 185116 | 185360 | 185473 | 185574 | 185853 | 186096 | 186357 | 186619 | 186794
|  | DG | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490
7 | 3F | SL No 540430038843 (EB Unit) | 582999 | 583682 | 584343 | 585017 | 585402 | 585741 | 586480 | 587202 | 587948 | 588648 | 589264 | 589747 | 590057 | 590772 | 591465 | 592158 | 592854 | 593597 | 594009 | 594357 | 595057 | 595730 | 596454 | 597135 | 597777 | 598255 | 598732 | 599462 | 600149 | 600853 | 601589 | 602012
|  | DG | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192
8 | 3F | SL No 540430038848 (EB Unit) | 113483 | 113597 | 113702 | 113838 | 113926 | 114016 | 114144 | 114264 | 114386 | 114504 | 114613 | 114729 | 114840 | 114967 | 115097 | 115219 | 115354 | 115480 | 115602 | 115702 | 115825 | 115930 | 116053 | 116169 | 116284 | 116379 | 116484 | 116617 | 116730 | 116840 | 116971 | 117032
|  | DG | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332
1 | 3F | AHU1 | 62404 | 62511 | 62609 | 62696 | 62742 | 62742 | 62850 | 62953 | 63045 | 63142 | 63219 | 63268 | 63268 | 63366 | 63457 | 63538 | 63619 | 63701 | 63745 | 63745 | 63851 | 63949 | 64036 | 64125 | 64208 | 64213 | 64213 | 64311 | 64385 | 64464 | 64540 | 64570
|  | DG | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004
2 | 3F | AHU2 | 64476 | 64566 | 64641 | 64701 | 64730 | 64730 | 64797 | 64850 | 64900 | 64947 | 64987 | 65020 | 65020 | 65080 | 65143 | 65193 | 65247 | 65297 | 65326 | 65326 | 65391 | 65441 | 65504 | 65559 | 65623 | 65636 | 65636 | 65718 | 65800 | 65879 | 65959 | 65986
|  | DG | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013
3 | 3F | AHU3 | 77898 | 77987 | 78075 | 78177 | 78232 | 78232 | 78355 | 78465 | 78570 | 78649 | 78752 | 78808 | 78808 | 78912 | 79017 | 79111 | 79220 | 79309 | 79361 | 79361 | 79461 | 79566 | 79681 | 79787 | 79889 | 79947 | 79947 | 80045 | 80156 | 80260 | 80362 | 80394
|  | DG | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166
4 | 3F | AHU4 | 52893 | 52996 | 53093 | 53190 | 53247 | 53247 | 53359 | 53466 | 53570 | 53657 | 53746 | 53798 | 53798 | 53885 | 53963 | 54048 | 54124 | 54198 | 54228 | 54228 | 54311 | 54385 | 54465 | 54545 | 54616 | 54621 | 54621 | 54708 | 54802 | 54899 | 54990 | 55029
|  | DG | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884
.
1 | 3F | AHU1 - BTU | 448252 | 448760 | 449035 | 449440 | 449627 | 449627 | 450163 | 450658 | 451051 | 451376 | 451693 | 451854 | 451854 | 452483 | 453013 | 453530 | 453919 | 454388 | 454569 | 454569 | 455081 | 455505 | 455965 | 456401 | 456828 | 456874 | 456874 | 457460 | 457953 | 458431 | 458818 | 459002
2 | 3F | AHU2 - BTU | 421761 | 422216 | 422595 | 423039 | 423318 | 423318 | 423880 | 424444 | 424901 | 425248 | 425560 | 425749 | 425749 | 426281 | 426829 | 427298 | 427709 | 428245 | 428450 | 428450 | 429092 | 429511 | 429927 | 430356 | 430712 | 430786 | 430786 | 431289 | 431714 | 432158 | 432472 | 432663
3 | 3F | AHU3 - BTU | 458458 | 459070 | 459479 | 460083 | 460386 | 460386 | 461252 | 462013 | 462597 | 463040 | 463420 | 463688 | 463688 | 464468 | 465076 | 465721 | 466175 | 466820 | 467077 | 467077 | 467827 | 468370 | 468893 | 469469 | 469891 | 470202 | 470202 | 470882 | 471434 | 472006 | 472497 | 472756
4 | 3F | AHU4 - BTU | 509335 | 510408 | 511327 | 512150 | 512641 | 512641 | 513641 | 514660 | 515522 | 516241 | 516958 | 517530 | 517530 | 518611 | 519578 | 520388 | 521299 | 522240 | 522505 | 522505 | 523503 | 524497 | 525352 | 526280 | 527085 | 527217 | 527217 | 528206 | 529090 | 529957 | 530867 | 531216
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter |  | 2026-07-01 | 2026-07-02 | 2026-07-03 | 2026-07-04 | 2026-07-05 | 2026-07-06 | 2026-07-07 | 2026-07-08 | 2026-07-09 | 2026-07-10 | 2026-07-11 | 2026-07-12 | 2026-07-13 | 2026-07-14 | 2026-07-15 | 2026-07-16 | 2026-07-17 | 2026-07-18 | 2026-07-19 | 2026-07-20 | 2026-07-21 | 2026-07-22 | 2026-07-23 | 2026-07-24 | 2026-07-25 | 2026-07-26 | 2026-07-27 | 2026-07-28 | 2026-07-29 | 2026-07-30 | 2026-07-31 | Consumption
|  |  |  | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time |  | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [33 empty] | EB
3 | 3F | AHU3 | [33 empty] | AHU
|  | DG | [33 empty] | BTU
4 | 3F | AHU4 | [33 empty] | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption
|  |  |  | JUNE - 2026 EV METER READING | [29 empty] | JUNE - 2026 EV METER READING
Sr.No | Location | Meter | Previous Reading | 2026-07-01 | 2026-07-02 | 2026-07-03 | 2026-07-04 | 2026-07-05 | 2026-07-06 | 2026-07-07 | 2026-07-08 | 2026-07-09 | 2026-07-10 | 2026-07-11 | 2026-07-12 | 2026-07-13 | 2026-07-14 | 2026-07-15 | 2026-07-16 | 2026-07-17 | 2026-07-18 | 2026-07-19 | 2026-07-20 | 2026-07-21 | 2026-07-22 | 2026-07-23 | 2026-07-24 | 2026-07-25 | 2026-07-26 | 2026-07-27 | 2026-07-28 | 2026-07-29 | 2026-07-30 | 2026-07-31 | Consumption
|  |  |  | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170 | 3356 | 3368 | 3395 | 3405 | 3405 | 3405 | 3405 | 3431 | 3443 | 3482 | 3499 | 3499 | 3499 | 3499 | 3524 | 3532 | 3532 | 3560 | 3560 | 3560 | 3587 | 3609 | 3609 | 3631 | 3678 | 3678 | 3678 | 3678 | 3715 | 3740 | 3781 | 3826
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170 | [31 empty] | 45

## Aug-2026
AUGUST - 2026
Sr.No | Location | Meter | Previous Reading | 2026-08-01 | 2026-08-02 | 2026-08-03 | 2026-08-04 | 2026-08-05 | 2026-08-06 | 2026-08-07 | 2026-08-08 | 2026-08-09 | 2026-08-10 | 2026-08-11 | 2026-08-12 | 2026-08-13 | 2026-08-14 | 2026-08-15 | 2026-08-16 | 2026-08-17 | 2026-08-18 | 2026-08-19 | 2026-08-20 | 2026-08-21 | 2026-08-22 | 2026-08-23 | 2026-08-24 | 2026-08-25 | 2026-08-26 | 2026-08-27 | 2026-08-28 | 2026-08-29 | 2026-08-30 | 2026-08-31 | Consumption
|  |  |  | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 217557 | 210554 | 210800 | 211054 | 211245 | 211447 | 211710 | 211951 | 212208 | 212453 | 212678 | 212890 | 213089 | 213341 | 213595 | 213844 | 214099 | 214346 | 214550 | 214746 | 214991 | 215245 | 215310 | 215762 | 215959 | 216204 | 216400 | 216663 | 216907 | 217151 | 217410 | 217557
|  | DG | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 314041 | 304225 | 304577 | 304934 | 305189 | 305452 | 305826 | 306176 | 306539 | 306885 | 307205 | 307484 | 307743 | 308105 | 308467 | 308830 | 309196 | 309540 | 309816 | 310071 | 310418 | 310784 | 311167 | 311529 | 311864 | 312133 | 312389 | 312762 | 313109 | 313457 | 313830 | 314041
|  | DG | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 166606 | 161040 | 161246 | 161453 | 161591 | 161720 | 161940 | 162137 | 162342 | 162539 | 162725 | 162874 | 163000 | 163202 | 163405 | 163616 | 163823 | 164025 | 164153 | 164260 | 164468 | 164682 | 164682 | 165121 | 165322 | 165471 | 165600 | 165829 | 166037 | 166254 | 166475 | 166606
|  | DG | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459
6 | 3F | SL No 540430038646 (EB Unit) | 186794 | 180108 | 180355 | 180610 | 180732 | 180853 | 181122 | 181389 | 181656 | 181902 | 182148 | 182302 | 182423 | 182697 | 182975 | 183255 | 183520 | 183771 | 183905 | 184030 | 184297 | 184573 | 184850 | 185116 | 185360 | 185473 | 185574 | 185853 | 186096 | 186357 | 186619 | 186794
|  | DG | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490
7 | 3F | SL No 540430038843 (EB Unit) | 602012 | 583682 | 584343 | 585017 | 585402 | 585741 | 586480 | 587202 | 587948 | 588648 | 589264 | 589747 | 590057 | 590772 | 591465 | 592158 | 592854 | 593597 | 594009 | 594357 | 595057 | 595730 | 596454 | 597135 | 597777 | 598255 | 598732 | 599462 | 600149 | 600853 | 601589 | 602012
|  | DG | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192
8 | 3F | SL No 540430038848 (EB Unit) | 117032 | 113597 | 113702 | 113838 | 113926 | 114016 | 114144 | 114264 | 114386 | 114504 | 114613 | 114729 | 114840 | 114967 | 115097 | 115219 | 115354 | 115480 | 115602 | 115702 | 115825 | 115930 | 116053 | 116169 | 116284 | 116379 | 116484 | 116617 | 116730 | 116840 | 116971 | 117032
|  | DG | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332
1 | 3F | AHU1 | 64570 | 62511 | 62609 | 62696 | 62742 | 62742 | 62850 | 62953 | 63045 | 63142 | 63219 | 63268 | 63268 | 63366 | 63457 | 63538 | 63619 | 63701 | 63745 | 63745 | 63851 | 63949 | 64036 | 64125 | 64208 | 64213 | 64213 | 64311 | 64385 | 64464 | 64540 | 64570
|  | DG | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004
2 | 3F | AHU2 | 65986 | 64566 | 64641 | 64701 | 64730 | 64730 | 64797 | 64850 | 64900 | 64947 | 64987 | 65020 | 65020 | 65080 | 65143 | 65193 | 65247 | 65297 | 65326 | 65326 | 65391 | 65441 | 65504 | 65559 | 65623 | 65636 | 65636 | 65718 | 65800 | 65879 | 65959 | 65986
|  | DG | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013
3 | 3F | AHU3 | 80394 | 77987 | 78075 | 78177 | 78232 | 78232 | 78355 | 78465 | 78570 | 78649 | 78752 | 78808 | 78808 | 78912 | 79017 | 79111 | 79220 | 79309 | 79361 | 79361 | 79461 | 79566 | 79681 | 79787 | 79889 | 79947 | 79947 | 80045 | 80156 | 80260 | 80362 | 80394
|  | DG | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166
4 | 3F | AHU4 | 55029 | 52996 | 53093 | 53190 | 53247 | 53247 | 53359 | 53466 | 53570 | 53657 | 53746 | 53798 | 53798 | 53885 | 53963 | 54048 | 54124 | 54198 | 54228 | 54228 | 54311 | 54385 | 54465 | 54545 | 54616 | 54621 | 54621 | 54708 | 54802 | 54899 | 54990 | 55029
|  | DG | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884
.
1 | 3F | AHU1 - BTU | 459002 | 448760 | 449035 | 449440 | 449627 | 449627 | 450163 | 450658 | 451051 | 451376 | 451693 | 451854 | 451854 | 452483 | 453013 | 453530 | 453919 | 454388 | 454569 | 454569 | 455081 | 455505 | 455965 | 456401 | 456828 | 456874 | 456874 | 457460 | 457953 | 458431 | 458818 | 459002
2 | 3F | AHU2 - BTU | 432663 | 422216 | 422595 | 423039 | 423318 | 423318 | 423880 | 424444 | 424901 | 425248 | 425560 | 425749 | 425749 | 426281 | 426829 | 427298 | 427709 | 428245 | 428450 | 428450 | 429092 | 429511 | 429927 | 430356 | 430712 | 430786 | 430786 | 431289 | 431714 | 432158 | 432472 | 432663
3 | 3F | AHU3 - BTU | 472756 | 459070 | 459479 | 460083 | 460386 | 460386 | 461252 | 462013 | 462597 | 463040 | 463420 | 463688 | 463688 | 464468 | 465076 | 465721 | 466175 | 466820 | 467077 | 467077 | 467827 | 468370 | 468893 | 469469 | 469891 | 470202 | 470202 | 470882 | 471434 | 472006 | 472497 | 472756
4 | 3F | AHU4 - BTU | 531216 | 510408 | 511327 | 512150 | 512641 | 512641 | 513641 | 514660 | 515522 | 516241 | 516958 | 517530 | 517530 | 518611 | 519578 | 520388 | 521299 | 522240 | 522505 | 522505 | 523503 | 524497 | 525352 | 526280 | 527085 | 527217 | 527217 | 528206 | 529090 | 529957 | 530867 | 531216
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter |  | 2026-08-01 | 2026-08-02 | 2026-08-03 | 2026-08-04 | 2026-08-05 | 2026-08-06 | 2026-08-07 | 2026-08-08 | 2026-08-09 | 2026-08-10 | 2026-08-11 | 2026-08-12 | 2026-08-13 | 2026-08-14 | 2026-08-15 | 2026-08-16 | 2026-08-17 | 2026-08-18 | 2026-08-19 | 2026-08-20 | 2026-08-21 | 2026-08-22 | 2026-08-23 | 2026-08-24 | 2026-08-25 | 2026-08-26 | 2026-08-27 | 2026-08-28 | 2026-08-29 | 2026-08-30 | 2026-08-31 | Consumption
|  |  |  | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [33 empty] | EB
3 | 3F | AHU3 | [33 empty] | AHU
|  | DG | [33 empty] | BTU
4 | 3F | AHU4 | [33 empty] | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption
|  |  |  | AUGUST - 2026 EV METER READING | [29 empty] | JUNE - 2026 EV METER READING
Sr.No | Location | Meter | Previous Reading | 2026-08-01 | 2026-08-02 | 2026-08-03 | 2026-08-04 | 2026-08-05 | 2026-08-06 | 2026-08-07 | 2026-08-08 | 2026-08-09 | 2026-08-10 | 2026-08-11 | 2026-08-12 | 2026-08-13 | 2026-08-14 | 2026-08-15 | 2026-08-16 | 2026-08-17 | 2026-08-18 | 2026-08-19 | 2026-08-20 | 2026-08-21 | 2026-08-22 | 2026-08-23 | 2026-08-24 | 2026-08-25 | 2026-08-26 | 2026-08-27 | 2026-08-28 | 2026-08-29 | 2026-08-30 | 2026-08-31 | Consumption
|  |  |  | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170 | 3826 | 3368 | 3395 | 3405 | 3405 | 3405 | 3405 | 3431 | 3443 | 3482 | 3499 | 3499 | 3499 | 3499 | 3524 | 3532 | 3532 | 3560 | 3560 | 3560 | 3587 | 3609 | 3609 | 3631 | 3678 | 3678 | 3678 | 3678 | 3715 | 3740 | 3781 | 3826
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170 |  | Mon: 45

## Jun-2026
JUNE - 2026
Sr.No | Location | Meter | Previous Reading | 2026-06-01 | 2026-06-02 | 2026-06-03 | 2026-06-04 | 2026-06-05 | 2026-06-06 | 2026-06-07 | 2026-06-08 | 2026-06-09 | 2026-06-10 | 2026-06-11 | 2026-06-12 | 2026-06-13 | 2026-06-14 | 2026-06-15 | 2026-06-16 | 2026-06-17 | 2026-06-18 | 2026-06-19 | 2026-06-20 | 2026-06-21 | 2026-06-22 | 2026-06-23 | 2026-06-24 | 2026-06-25 | 2026-06-26 | 2026-06-27 | 2026-06-28 | 2026-06-29 | 2026-06-30 | Consumption
|  |  |  | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 203246 | 203478 | 203736 | 203987 | 204223 | 204466 | 204671 | 204876 | 205060 | 205245 | 205506 | 205765 | 206011 | 206216 | 206421 | 206679 | 206930 | 207193 | 207440 | 207689 | 207908 | 208110 | 208360 | 208616 | 208877 | 209124 | 209375 | 209584 | 209799 | 210051 | 210307
|  | DG | 4343 | 4343 | 4343 | 4343 | 4343 | 4343 | 4343 | 4343 | 4412 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486 | 4486
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 293912 | 294244 | 294613 | 294973 | 295313 | 295654 | 295928 | 296200 | 296455 | 296712 | 297095 | 297467 | 297817 | 298090 | 298360 | 298731 | 299094 | 299475 | 299832 | 300190 | 300482 | 300746 | 301109 | 301477 | 301858 | 302214 | 302574 | 302855 | 303142 | 303503 | 303867
|  | DG | 6492 | 6492 | 6492 | 6492 | 6492 | 6492 | 6492 | 6492 | 6599 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713 | 6713
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 155368 | 155561 | 155767 | 155872 | 156167 | 156360 | 156506 | 156633 | 156776 | 156919 | 157131 | 157342 | 157537 | 157667 | 157783 | 157992 | 158186 | 158409 | 158598 | 158790 | 158938 | 159067 | 159278 | 159493 | 159710 | 159915 | 160116 | 160267 | 160407 | 160623 | 160838
|  | DG | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3327 | 3390 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459 | 3459
6 | 3F | SL No 540430038646 (EB Unit) | 173457 | 173696 | 173957 | 174206 | 174453 | 174694 | 174828 | 174919 | 175108 | 175282 | 175559 | 175812 | 176061 | 176168 | 176268 | 176513 | 176754 | 177006 | 177266 | 177498 | 177632 | 177722 | 177962 | 178221 | 178506 | 178761 | 179023 | 179166 | 179314 | 179563 | 179845
|  | DG | 4311 | 4311 | 4311 | 4311 | 4311 | 4311 | 4311 | 4311 | 4395 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490 | 4490
7 | 3F | SL No 540430038843 (EB Unit) | 565472 | 566108 | 566781 | 567438 | 568082 | 568742 | 569192 | 569499 | 569499 | 569989 | 570454 | 571141 | 571814 | 572447 | 572820 | 573100 | 573823 | 574514 | 575218 | 575872 | 575638 | 577093 | 578071 | 578778 | 579457 | 580131 | 580812 | 581259 | 581611 | 582306 | 582999
|  | DG | 11782 | 11782 | 11782 | 11782 | 11782 | 11782 | 11782 | 11782 | 11986 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192 | 12192
8 | 3F | SL No 540430038848 (EB Unit) | 109469 | 109597 | 109740 | 109888 | 110021 | 110165 | 110298 | 110432 | 110540 | 110659 | 110814 | 110968 | 111094 | 111205 | 111324 | 111467 | 111594 | 111740 | 111864 | 112011 | 112152 | 112282 | 112430 | 112565 | 112683 | 112809 | 112921 | 113039 | 113159 | 113338 | 113483
|  | DG | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2240 | 2289 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332 | 2332
1 | 3F | AHU1 | 60602 | 60700 | 60805 | 60893 | 60975 | 61058 | 61109 | 61109 | 61168 | 61206 | 61279 | 61346 | 61402 | 61420 | 61420 | 61489 | 61545 | 61612 | 61672 | 61730 | 61763 | 61763 | 61840 | 61911 | 61990 | 62075 | 62160 | 62196 | 62196 | 62310 | 62404
|  | DG | 1992 | 1922 | 1922 | 1929 | 1929 | 1929 | 1929 | 1929 | 1972 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004 | 2004
2 | 3F | AHU2 | 62620 | 62701 | 62779 | 62853 | 62926 | 63001 | 63042 | 63042 | 63090 | 63139 | 63220 | 63291 | 63367 | 63388 | 63388 | 63474 | 63548 | 63622 | 63691 | 63767 | 63805 | 63805 | 63887 | 63973 | 64066 | 64171 | 64246 | 64284 | 64284 | 64388 | 64476
|  | DG | 1945 | 1945 | 1945 | 1945 | 1945 | 1945 | 1945 | 1945 | 1978 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013 | 2013
3 | 3F | AHU3 | 75704 | 75802 | 75907 | 75991 | 76075 | 76152 | 76206 | 76206 | 76262 | 76319 | 76420 | 76515 | 76608 | 76659 | 76659 | 76754 | 76833 | 76913 | 76997 | 77075 | 77120 | 77120 | 77219 | 77330 | 77424 | 77523 | 77622 | 77671 | 77671 | 77797 | 77898
|  | DG | 2075 | 2075 | 2075 | 2075 | 2075 | 2075 | 2075 | 2075 | 2121 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166 | 2166
4 | 3F | AHU4 | 51063 | 51141 | 51216 | 51290 | 51353 | 51417 | 51436 | 51436 | 51489 | 51544 | 51633 | 51719 | 51802 | 51804 | 51804 | 51886 | 51960 | 52033 | 52108 | 52176 | 52217 | 52217 | 52303 | 52392 | 52467 | 52545 | 52618 | 52663 | 52663 | 52782 | 52893
|  | DG | 1793 | 1793 | 1793 | 1793 | 1793 | 1793 | 1793 | 1793 | 1844 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884 | 1884
.
1 | 3F | AHU1 - BTU | 436512 | 437036 | 437505 | 437972 | 438400 | 438774 | 438930 | 438930 | 439432 | 439996 | 440530 | 441100 | 441493 | 441642 | 441642 | 442135 | 442586 | 443090 | 443495 | 443908 | 444122 | 444122 | 444658 | 445174 | 445659 | 446257 | 446737 | 447059 | 447059 | 447656 | 448252
2 | 3F | AHU2 - BTU | 410185 | 410652 | 411116 | 411652 | 411997 | 412469 | 412713 | 412713 | 413193 | 413707 | 414175 | 414708 | 415135 | 415332 | 415332 | 415824 | 416263 | 416766 | 417208 | 417664 | 417933 | 417933 | 418442 | 448890 | 419367 | 419910 | 420368 | 420611 | 420611 | 421191 | 421761
3 | 3F | AHU3 - BTU | 444498 | 445220 | 445724 | 446303 | 446812 | 447291 | 447578 | 447578 | 448286 | 448952 | 449387 | 450006 | 450377 | 450684 | 450684 | 451371 | 451805 | 452224 | 452645 | 453039 | 453324 | 453324 | 453978 | 454566 | 455079 | 455675 | 456327 | 456734 | 456734 | 457569 | 458458
4 | 3F | AHU4 - BTU | 489616 | 490429 | 491240 | 492012 | 492777 | 493455 | 493710 | 493710 | 494532 | 495500 | 496239 | 497238 | 498008 | 498190 | 498190 | 499113 | 499861 | 500719 | 501571 | 502320 | 502682 | 502682 | 503553 | 504389 | 505322 | 506094 | 506963 | 507414 | 507414 | 508346 | 509335
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter |  | 2026-06-01 | 2026-06-02 | 2026-06-03 | 2026-06-04 | 2026-06-05 | 2026-06-06 | 2026-06-07 | 2026-06-08 | 2026-06-09 | 2026-06-10 | 2026-06-11 | 2026-06-12 | 2026-06-13 | 2026-06-14 | 2026-06-15 | 2026-06-16 | 2026-06-17 | 2026-06-18 | 2026-06-19 | 2026-06-20 | 2026-06-21 | 2026-06-22 | 2026-06-23 | 2026-06-24 | 2026-06-25 | 2026-06-26 | 2026-06-27 | 2026-06-28 | 2026-06-29 | 2026-06-30 | Consumption
|  |  |  | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time |  | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [32 empty] | EB
3 | 3F | AHU3 | [32 empty] | AHU
|  | DG | [32 empty] | BTU
4 | 3F | AHU4 | [32 empty] | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU |  | 2026-06-23: 448; 2026-06-24: 477
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption
JUNE - 2026 EV METER READING
Sr.No | Location | Meter | Previous Reading | 2026-06-01 | 2026-06-02 | 2026-06-03 | 2026-06-04 | 2026-06-05 | 2026-06-06 | 2026-06-07 | 2026-06-08 | 2026-06-09 | 2026-06-10 | 2026-06-11 | 2026-06-12 | 2026-06-13 | 2026-06-14 | 2026-06-15 | 2026-06-16 | 2026-06-17 | 2026-06-18 | 2026-06-19 | 2026-06-20 | 2026-06-21 | 2026-06-22 | 2026-06-23 | 2026-06-24 | 2026-06-25 | 2026-06-26 | 2026-06-27 | 2026-06-28 | 2026-06-29 | 2026-06-30 | Consumption
|  |  |  | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170 | 3124 | 3124 | 3150 | 3167 | 3167 | 3167 | 3167 | 3167 | 3167 | 3177 | 3200 | 3200 | 3227 | 3227 | 3227 | 3227 | 3254 | 3265 | 3289 | 3289 | 3289 | 3289 | 3312 | 3312 | 3327 | 3327 | 3327 | 3327 | 3327 | 3344 | 3356
Sr.No | Location | Meter | [31 empty] | Consumption
|  |  |  | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170

## May-2026
May - 2026
Sr.No | Location | Meter | Previous Reading | 2026-05-01 | 2026-05-02 | 2026-05-03 | 2026-05-04 | 2026-05-05 | 2026-05-06 | 2026-05-07 | 2026-05-08 | 2026-05-09 | 2026-05-10 | 2026-05-11 | 2026-05-12 | 2026-05-13 | 2026-05-14 | 2026-05-15 | 2026-05-16 | 2026-05-17 | 2026-05-18 | 2026-05-19 | 2026-05-20 | 2026-05-21 | 2026-05-22 | 2026-05-23 | 2026-05-24 | 2026-05-25 | 2026-05-26 | 2026-05-27 | 2026-05-28 | 2026-05-29 | 2026-05-30 | 2026-05-31 | Consumption
|  |  |  | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 196078 | 196329 | 196545 | 196744 | 196988 | 197243 | 197487 | 197732 | 197972 | 198189 | 198400 | 198652 | 198904 | 199142 | 199401 | 199622 | 199832 | 200036 | 200278 | 200522 | 200776 | 201019 | 201267 | 201486 | 201682 | 201918 | 202153 | 202362 | 202608 | 202841 | 203035 | 203246
|  | DG | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4339 | 4339 | 4339 | 4339 | 4339 | 4339 | 4343
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 283914 | 284312 | 284601 | 284864 | 285209 | 285572 | 285919 | 286267 | 286606 | 286898 | 287179 | 287540 | 287501 | 288125 | 288608 | 288923 | 289202 | 289467 | 289812 | 290159 | 290520 | 290865 | 291221 | 291513 | 291769 | 292099 | 292432 | 292708 | 293056 | 293381 | 293636 | 293912
|  | DG | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6487 | 6487 | 6487 | 6487 | 6487 | 6487 | 6492
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 149904 | 150177 | 150283 | 150409 | 150621 | 150832 | 151045 | 151252 | 151446 | 151583 | 151719 | 151919 | 152123 | 152308 | 152507 | 152684 | 152831 | 152949 | 153150 | 153347 | 153549 | 153750 | 153949 | 154083 | 154204 | 154400 | 154588 | 154716 | 154913 | 155098 | 155228 | 155368
|  | DG | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3324 | 3324 | 3324 | 3324 | 3324 | 3327 | 3327
6 | 3F | SL No 540430038646 (EB Unit) | 166898 | 167179 | 167330 | 167429 | 167673 | 167940 | 168183 | 168435 | 168672 | 168821 | 168917 | 169119 | 169447 | 169687 | 169946 | 170188 | 170308 | 170432 | 170704 | 170980 | 171268 | 171542 | 171801 | 171944 | 172078 | 172368 | 172623 | 172745 | 172997 | 173241 | 173347 | 173457
|  | DG | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4308 | 4308 | 4308 | 4308 | 4308 | 4311 | 4311
7 | 3F | SL No 540430038843 (EB Unit) | 548563 | 549307 | 549711 | 550092 | 550821 | 551534 | 552181 | 552862 | 553486 | 553905 | 554260 | 554964 | 555661 | 556256 | 556942 | 557560 | 557872 | 558164 | 558867 | 559513 | 560204 | 560880 | 561550 | 561821 | 562085 | 562720 | 563336 | 563585 | 564216 | 564857 | 565149 | 565472
|  | DG | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11775 | 11775 | 11775 | 11775 | 11775 | 11775 | 11782
8 | 3F | SL No 540430038848 (EB Unit) | 105288 | 105417 | 105552 | 105660 | 105794 | 105931 | 106066 | 106194 | 106341 | 106459 | 106584 | 106721 | 106870 | 107000 | 107133 | 107265 | 107398 | 107529 | 107689 | 107842 | 107991 | 108140 | 108302 | 108421 | 108533 | 108679 | 108838 | 108975 | 109126 | 109254 | 109359 | 109469
|  | DG | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2239 | 2239 | 2240 | 2240
1 | 3F | AHU1 | 59001 | 59111 | 59175 | 59175 | 59235 | 59302 | 59360 | 59420 | 59475 | 59507 | 59507 | 59567 | 59625 | 59680 | 59744 | 59806 | 59820 | 59821 | 59890 | 59980 | 60061 | 60142 | 60227 | 60249 | 60249 | 60346 | 60441 | 60442 | 60523 | 60598 | 60601 | 60602
|  | DG | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923
2 | 3F | AHU2 | 61050 | 61184 | 61261 | 61261 | 61349 | 61442 | 61511 | 61576 | 61641 | 61674 | 61674 | 61733 | 61790 | 61849 | 61912 | 61978 | 61979 | 61980 | 62049 | 62114 | 62176 | 62238 | 62299 | 62299 | 62299 | 62369 | 62444 | 62445 | 62517 | 62583 | 62620 | 62620
|  | DG | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1945 | 1945 | 1945 | 1945 | 1945 | 1945 | 1945
3 | 3F | AHU3 | 73971 | 74060 | 74122 | 74122 | 74208 | 74302 | 74372 | 74453 | 74522 | 74593 | 74593 | 74674 | 74747 | 74813 | 74874 | 74940 | 74941 | 74941 | 75006 | 75064 | 75125 | 75183 | 75249 | 75270 | 75270 | 75382 | 75478 | 75482 | 75569 | 75652 | 75704 | 75704
|  | DG | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2075 | 2075 | 2075 | 2075 | 2075 | 2075 | 2075
4 | 3F | AHU4 | 49701 | 49769 | 49815 | 49815 | 49881 | 49949 | 50004 | 50066 | 50120 | 50151 | 50152 | 50212 | 50262 | 50319 | 50374 | 50425 | 50425 | 50426 | 50490 | 50540 | 50603 | 50662 | 50729 | 50731 | 50732 | 50814 | 50903 | 50907 | 50989 | 51058 | 51062 | 51063
|  | DG | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1793 | 1793 | 1793 | 1793 | 1793 | 1793 | 1793
1 | 3F | AHU1 - BTU | 426274 | 426951 | 427390 | 427390 | 427816 | 428265 | 428679 | 429011 | 429385 | 429560 | 429560 | 430130 | 430629 | 431087 | 431492 | 431834 | 431925 | 431925 | 432469 | 432939 | 433355 | 433865 | 434294 | 434427 | 434427 | 434926 | 435534 | 435585 | 436083 | 436485 | 436512 | 436512
2 | 3F | AHU2 - BTU | 400631 | 401127 | 401304 | 401304 | 401788 | 402146 | 402492 | 402846 | 403168 | 403360 | 403360 | 403862 | 404354 | 404809 | 405157 | 405515 | 405515 | 405515 | 406104 | 406574 | 407006 | 407568 | 407946 | 407946 | 407946 | 408445 | 409000 | 409048 | 409539 | 409968 | 410185 | 410185
3 | 3F | AHU3 - BTU | 431431 | 432150 | 432559 | 432559 | 433223 | 433761 | 434231 | 434563 | 434927 | 435320 | 435320 | 436210 | 436755 | 437369 | 437815 | 438277 | 438277 | 438277 | 439031 | 439578 | 440160 | 440750 | 441339 | 441603 | 441603 | 442314 | 443038 | 443121 | 443733 | 444194 | 444498 | 444498
4 | 3F | AHU4 - BTU | 473317 | 474228 | 474694 | 474694 | 475457 | 476194 | 476924 | 477604 | 478257 | 478600 | 478600 | 479421 | 480156 | 480854 | 481509 | 482114 | 482185 | 482185 | 483059 | 483697 | 484366 | 485107 | 485795 | 485945 | 485945 | 486741 | 487814 | 487967 | 488800 | 489515 | 489616 | 489616
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter |  | 2026-05-01 | 2026-05-02 | 2026-05-03 | 2026-05-04 | 2026-05-05 | 2026-05-06 | 2026-05-07 | 2026-05-08 | 2026-05-09 | 2026-05-10 | 2026-05-11 | 2026-05-12 | 2026-05-13 | 2026-05-14 | 2026-05-15 | 2026-05-16 | 2026-05-17 | 2026-05-18 | 2026-05-19 | 2026-05-20 | 2026-05-21 | 2026-05-22 | 2026-05-23 | 2026-05-24 | 2026-05-25 | 2026-05-26 | 2026-05-27 | 2026-05-28 | 2026-05-29 | 2026-05-30 | 2026-05-31 | Consumption
|  |  |  | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time |  | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [33 empty] | EB
3 | 3F | AHU3 | [33 empty] | AHU
|  | DG | [33 empty] | BTU
4 | 3F | AHU4 | [33 empty] | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption
May - 2026 EV METER READING
Sr.No | Location | Meter | Previous Reading | 2026-05-01 | 2026-05-02 | 2026-05-03 | 2026-05-04 | 2026-05-05 | 2026-05-06 | 2026-05-07 | 2026-05-08 | 2026-05-09 | 2026-05-10 | 2026-05-11 | 2026-05-12 | 2026-05-13 | 2026-05-14 | 2026-05-15 | 2026-05-16 | 2026-05-17 | 2026-05-18 | 2026-05-19 | 2026-05-20 | 2026-05-21 | 2026-05-22 | 2026-05-23 | 2026-05-24 | 2026-05-25 | 2026-05-26 | 2026-05-27 | 2026-05-28 | 2026-05-29 | 2026-05-30 | 2026-05-31 | Consumption
|  |  |  | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170 | 2870 | 2877 | 2877 | 2877 | 2877 | 2886 | 2893 | 2893 | 2900 | 2900 | 2900 | 2900 | 2914 | 2942 | 2955 | 2972 | 2972 | 2972 | 2997 | 3022 | 3032 | 3059 | 3076 | 3076 | 3076 | 3076 | 3099 | 3099 | 3124 | 3124 | 3124 | 3124
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170

## April-2026
April - 2026
Sr.No | Location | Meter | Previous Reading | 2026-04-01 | 2026-04-02 | 2026-04-03 | 2026-04-04 | 2026-04-05 | 2026-04-06 | 2026-04-07 | 2026-04-08 | 2026-04-09 | 2026-04-10 | 2026-04-11 | 2026-04-12 | 2026-04-13 | 2026-04-14 | 2026-04-15 | 2026-04-16 | 2026-04-17 | 2026-04-18 | 2026-04-19 | 2026-04-20 | 2026-04-21 | 2026-04-22 | 2026-04-23 | 2026-04-24 | 2026-04-25 | 2026-04-26 | 2026-04-27 | 2026-04-28 | 2026-04-29 | 2026-04-30 | Consumption
|  |  |  | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 188707 | 189123 | 189320 | 189538 | 189741 | 189949 | 190161 | 190419 | 190690 | 190946 | 191202 | 191403 | 191603 | 191870 | 192127 | 192390 | 192641 | 192912 | 193129 | 193328 | 193592 | 193854 | 194112 | 194369 | 194620 | 194833 | 195041 | 195292 | 195556 | 195813 | 196078
|  | DG | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.3 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 273490 | 274089 | 274381 | 274673 | 274947 | 275222 | 275511 | 275886 | 276282 | 276656 | 277020 | 277292 | 277559 | 277944 | 278324 | 278709 | 279075 | 279465 | 279746 | 280016 | 280397 | 280781 | 281152 | 281529 | 281886 | 282171 | 282447 | 282812 | 283201 | 283566 | 283914
|  | DG | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 143732 | 144105 | 144275 | 144415 | 144547 | 144696 | 144865 | 145101 | 145346 | 145503 | 145806 | 145945 | 146078 | 146322 | 146563 | 146772 | 147037 | 147286 | 147413 | 147529 | 147769 | 148006 | 148246 | 148476 | 148699 | 148853 | 148985 | 149200 | 149433 | 149662 | 149904
|  | DG | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316
6 | 3F | SL No 540430038646 (EB Unit) | 160213 | 160642 | 160877 | 160988 | 161082 | 161173 | 161261 | 161530 | 161795 | 162059 | 162320 | 162434 | 162516 | 162803 | 163074 | 163354 | 163619 | 163924 | 164045 | 164136 | 164396 | 164687 | 164971 | 165253 | 165535 | 165683 | 165800 | 166065 | 166337 | 166611 | 166898
|  | DG | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297
7 | 3F | SL No 540430038843 (EB Unit) | 528403 | 529732 | 530347 | 530777 | 531162 | 531674 | 532109 | 532851 | 533672 | 534410 | 535246 | 535602 | 536003 | 536803 | 537574 | 538394 | 539168 | 539950 | 540353 | 540688 | 541492 | 542247 | 543018 | 543788 | 544541 | 545059 | 545464 | 546206 | 547009 | 547765 | 548563
|  | DG | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747
8 | 3F | SL No 540430038848 (EB Unit) | 101290 | 101483 | 101577 | 101694 | 101810 | 101928 | 102051 | 102170 | 102297 | 102413 | 102536 | 102638 | 102748 | 102877 | 103011 | 103150 | 103298 | 103444 | 103565 | 103682 | 103830 | 103953 | 104115 | 104246 | 104395 | 104535 | 104669 | 104819 | 104982 | 105143 | 105288
|  | DG | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232
1 | 3F | AHU1 | 56137 | 56320 | 56448 | 56468 | 56468 | 56468 | 56493 | 56657 | 56836 | 57014 | 57199 | 57240 | 57241 | 57378 | 57536 | 57667 | 57812 | 57930 | 57951 | 57951 | 58060 | 58181 | 58295 | 58389 | 58487 | 58537 | 58537 | 58692 | 58760 | 58879 | 59001
|  | DG | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923
2 | 3F | AHU2 | 58488 | 58617 | 58695 | 58695 | 58695 | 58695 | 58743 | 58842 | 58910 | 58972 | 59064 | 59064 | 59065 | 59191 | 59343 | 59468 | 59594 | 59718 | 59731 | 59731 | 59859 | 59994 | 60131 | 60302 | 60431 | 60502 | 60502 | 60638 | 60787 | 60934 | 61050
|  | DG | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1940 | 1940 | 1940 | 1940
3 | 3F | AHU3 | 71032 | 71196 | 71310 | 71310 | 71364 | 71486 | 71534 | 71636 | 71741 | 71846 | 71972 | 71972 | 71972 | 72100 | 72180 | 72260 | 72330 | 72424 | 72505 | 72659 | 72854 | 72938 | 73026 | 73152 | 73275 | 73353 | 73432 | 73594 | 73721 | 73852 | 73971
|  | DG | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068
4 | 3F | AHU4 | 47765 | 47906 | 48032 | 48032 | 48032 | 48032 | 48033 | 48136 | 48201 | 48267 | 48337 | 48337 | 48369 | 48527 | 48620 | 48701 | 48769 | 48839 | 48851 | 48851 | 48936 | 49009 | 49092 | 49162 | 49234 | 49279 | 49332 | 49462 | 49547 | 49629 | 49701
|  | DG | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788
1 | 3F | AHU1 - BTU | 414628 | 415189 | 415568 | 415659 | 415659 | 415659 | 415659 | 416210 | 416607 | 417121 | 417535 | 417620 | 417620 | 418192 | 418717 | 419243 | 419741 | 420357 | 420429 | 420429 | 421020 | 421633 | 422282 | 422853 | 423297 | 423735 | 423735 | 424357 | 425049 | 425782 | 426274
2 | 3F | AHU2 - BTU | 390121 | 390737 | 391182 | 391218 | 391218 | 391218 | 391325 | 391834 | 392223 | 392604 | 392963 | 392963 | 392963 | 393469 | 393973 | 394494 | 394956 | 395469 | 395578 | 395578 | 396141 | 396609 | 397117 | 397759 | 398184 | 398557 | 398557 | 399178 | 399731 | 400245 | 400631
3 | 3F | AHU3 - BTU | 417583 | 418236 | 418594 | 418612 | 418787 | 419257 | 419582 | 419998 | 420397 | 420848 | 421274 | 421305 | 421305 | 421850 | 422329 | 422870 | 423362 | 423693 | 423987 | 424672 | 425784 | 426382 | 426897 | 427552 | 428062 | 428525 | 428896 | 430019 | 430582 | 431030 | 431431
4 | 3F | AHU4 - BTU | 456076 | 457006 | 457713 | 457812 | 457812 | 457812 | 457947 | 458733 | 459480 | 460167 | 460786 | 460858 | 460958 | 462079 | 462829 | 463651 | 464390 | 465069 | 465248 | 465248 | 466114 | 466872 | 467647 | 468395 | 468985 | 469490 | 469749 | 470843 | 471730 | 472605 | 473317
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter |  | 2026-04-01 | 2026-04-02 | 2026-04-03 | 2026-04-04 | 2026-04-05 | 2026-04-06 | 2026-04-07 | 2026-04-08 | 2026-04-09 | 2026-04-10 | 2026-04-11 | 2026-04-12 | 2026-04-13 | 2026-04-14 | 2026-04-15 | 2026-04-16 | 2026-04-17 | 2026-04-18 | 2026-04-19 | 2026-04-20 | 2026-04-21 | 2026-04-22 | 2026-04-23 | 2026-04-24 | 2026-04-25 | 2026-04-26 | 2026-04-27 | 2026-04-28 | 2026-04-29 | 2026-04-30 | Consumption
|  |  |  | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time |  | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [32 empty] | EB
3 | 3F | AHU3 | [32 empty] | AHU
|  | DG | [32 empty] | BTU
4 | 3F | AHU4 | [32 empty] | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption
April - 2026 EV METER READING
Sr.No | Location | Meter | Previous Reading | 2026-04-01 | 2026-04-02 | 2026-04-03 | 2026-04-04 | 2026-04-05 | 2026-04-06 | 2026-04-07 | 2026-04-08 | 2026-04-09 | 2026-04-10 | 2026-04-11 | 2026-04-12 | 2026-04-13 | 2026-04-14 | 2026-04-15 | 2026-04-16 | 2026-04-17 | 2026-04-18 | 2026-04-19 | 2026-04-20 | 2026-04-21 | 2026-04-22 | 2026-04-23 | 2026-04-24 | 2026-04-25 | 2026-04-26 | 2026-04-27 | 2026-04-28 | 2026-04-29 | 2026-04-30 | Consumption
|  |  |  | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170 | 2536 | 2560 | 2578 | 2578 | 2578 | 2578 | 2578 | 2585 | 2608 | 2621 | 2644 | 2644 | 2644 | 2644 | 2669 | 2678 | 2690 | 2705 | 2705 | 2705 | 2717 | 2741 | 2775 | 2791 | 2806 | 2806 | 2806 | 2818 | 2843 | 2859 | 2870
Sr.No | Location | Meter | [31 empty] | Consumption
|  |  |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170

## Mar-2026
Mar - 2026
Sr.No | Location | Meter | Previous Reading | 2026-03-01 | 2026-03-02 | 2026-03-03 | 2026-03-04 | 2026-03-05 | 2026-03-06 | 2026-03-07 | 2026-03-08 | 2026-03-09 | 2026-03-10 | 2026-03-11 | 2026-03-12 | 2026-03-13 | 2026-03-14 | 2026-03-15 | 2026-03-16 | 2026-03-17 | 2026-03-18 | 2026-03-19 | 2026-03-20 | 2026-03-21 | 2026-03-22 | 2026-03-23 | 2026-03-24 | 2026-03-25 | 2026-03-26 | 2026-03-27 | 2026-03-28 | 2026-03-29 | 2026-03-30 | 2026-03-31 | Consumption
|  |  |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 181312 | 181638 | 181888 | 182152 | 182357 | 182594 | 182840 | 183048 | 183252 | 183507 | 183763 | 184009 | 184265 | 184516 | 184738 | 184910 | 185169 | 185431 | 185691 | 185944 | 186184 | 186387 | 186589 | 186848 | 187117 | 187372 | 187628 | 187880 | 188102 | 188291 | 188563 | 188707
|  | DG | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329 | 4329
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 263065 | 263489 | 263854 | 264231 | 264505 | 264843 | 265196 | 265474 | 265743 | 266113 | 266484 | 266841 | 267212 | 267575 | 267841 | 268075 | 268454 | 268843 | 269218 | 269584 | 269931 | 270202 | 270464 | 270841 | 271233 | 271606 | 271974 | 272342 | 272637 | 272884 | 273280 | 273490
|  | DG | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472 | 6472
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 137256 | 137480 | 137712 | 137954 | 138089 | 138304 | 138541 | 138700 | 138851 | 139091 | 139332 | 139575 | 139837 | 140077 | 140236 | 140361 | 140614 | 140870 | 141125 | 141367 | 141598 | 141748 | 141874 | 142093 | 142356 | 142581 | 142803 | 143027 | 143205 | 143332 | 143591 | 143732
|  | DG | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316 | 3316
6 | 3F | SL No 540430038646 (EB Unit) | 153569 | 153747 | 154000 | 154277 | 154362 | 154614 | 154853 | 154969 | 155053 | 155336 | 155611 | 155891 | 156151 | 156430 | 156509 | 156577 | 156858 | 157116 | 157389 | 157634 | 157859 | 158015 | 158114 | 158400 | 158704 | 158981 | 159258 | 159507 | 159719 | 159799 | 160082 | 160213
|  | DG | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297 | 4297
7 | 3F | SL No 540430038843 (EB Unit) | 506717 | 507458 | 508242 | 509082 | 509409 | 510133 | 510895 | 511414 | 511903 | 512676 | 513427 | 514269 | 515084 | 515884 | 516418 | 516789 | 517601 | 518383 | 519214 | 520019 | 520787 | 521456 | 521929 | 522725 | 523573 | 524369 | 525166 | 525974 | 526680 | 527141 | 527964 | 528403
|  | DG | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747 | 11747
8 | 3F | SL No 540430038848 (EB Unit) | 97629 | 97781 | 97909 | 98037 | 98141 | 98265 | 98403 | 98507 | 98622 | 98749 | 98878 | 98993 | 99126 | 99243 | 99363 | 99452 | 99569 | 99690 | 99806 | 99924 | 100022 | 100105 | 100208 | 100330 | 100450 | 100571 | 100683 | 100812 | 100939 | 101054 | 101200 | 101290
|  | DG | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232 | 2232
1 | 3F | AHU1 | 52703 | 52761 | 52890 | 53045 | 53045 | 53214 | 53359 | 53462 | 53463 | 53592 | 53754 | 53922 | 54058 | 54212 | 54253 | 54253 | 54392 | 54549 | 54698 | 54808 | 54945 | 55050 | 55050 | 55198 | 55364 | 55501 | 55692 | 55784 | 55911 | 55911 | 56048 | 56137
|  | DG | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923
2 | 3F | AHU2 | 55794 | 55846 | 55939 | 56027 | 56027 | 56139 | 56226 | 56253 | 56254 | 56359 | 56518 | 56661 | 56777 | 56930 | 57013 | 57013 | 57164 | 57297 | 57451 | 57584 | 57695 | 57755 | 57755 | 57873 | 57988 | 58082 | 58186 | 58282 | 58356 | 58356 | 58453 | 58488
|  | DG | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911
3 | 3F | AHU3 | 68469 | 68545 | 68643 | 68740 | 68740 | 68835 | 68924 | 68972 | 68972 | 69059 | 69173 | 69290 | 69366 | 69489 | 69500 | 69500 | 69628 | 69738 | 69847 | 69972 | 70083 | 70196 | 70196 | 70321 | 70421 | 70525 | 70617 | 70725 | 70725 | 70858 | 70992 | 71032
|  | DG | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068
4 | 3F | AHU4 | 45373 | 45407 | 45525 | 45646 | 45646 | 45764 | 45888 | 45892 | 45892 | 46014 | 46133 | 46271 | 46335 | 46413 | 46421 | 46421 | 46631 | 46791 | 46919 | 47007 | 47082 | 47131 | 47131 | 47186 | 47256 | 47325 | 47387 | 47511 | 47588 | 47588 | 47720 | 47765
|  | DG | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788
1 | 3F | AHU1 - BTU | 403490 | 403619 | 404104 | 404520 | 404590 | 405024 | 405570 | 405845 | 405845 | 406401 | 407025 | 407461 | 407962 | 408360 | 408447 | 408450 | 408955 | 409501 | 410003 | 410383 | 410671 | 410849 | 410872 | 411414 | 411981 | 412482 | 412893 | 413316 | 413743 | 413743 | 414220 | 414628
2 | 3F | AHU2 - BTU | 378984 | 379118 | 379560 | 380025 | 380038 | 380494 | 381098 | 381285 | 381285 | 381828 | 382421 | 382954 | 383361 | 383832 | 384060 | 384063 | 384586 | 385108 | 385593 | 386018 | 386410 | 386559 | 386586 | 387120 | 387565 | 388032 | 388499 | 388838 | 389277 | 389277 | 389838 | 390121
3 | 3F | AHU3 - BTU | 406367 | 406550 | 406995 | 407436 | 407436 | 407791 | 408167 | 408388 | 408388 | 408920 | 409426 | 409967 | 410456 | 410758 | 410826 | 410826 | 411482 | 412020 | 412519 | 412856 | 413163 | 413479 | 413512 | 414009 | 414581 | 415186 | 415650 | 416100 | 416549 | 416549 | 417186 | 417583
4 | 3F | AHU4 - BTU | 440357 | 440473 | 440859 | 441312 | 441351 | 441904 | 442255 | 442283 | 442283 | 443094 | 444074 | 444925 | 445602 | 446161 | 446322 | 446358 | 447161 | 448035 | 448774 | 449455 | 449977 | 450348 | 450404 | 451069 | 451781 | 452512 | 453248 | 453960 | 454602 | 454602 | 455540 | 456076
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter |  | 2026-03-01 | 2026-03-02 | 2026-03-03 | 2026-03-04 | 2026-03-05 | 2026-03-06 | 2026-03-07 | 2026-03-08 | 2026-03-09 | 2026-03-10 | 2026-03-11 | 2026-03-12 | 2026-03-13 | 2026-03-14 | 2026-03-15 | 2026-03-16 | 2026-03-17 | 2026-03-18 | 2026-03-19 | 2026-03-20 | 2026-03-21 | 2026-03-22 | 2026-03-23 | 2026-03-24 | 2026-03-25 | 2026-03-26 | 2026-03-27 | 2026-03-28 | 2026-03-29 | 2026-03-30 | 2026-03-31 | Consumption
|  |  |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time |  | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [33 empty] | EB
3 | 3F | AHU3 | [33 empty] | AHU
|  | DG | [33 empty] | BTU
4 | 3F | AHU4 | [33 empty] | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption
Mar - 2026 EV METER READING
Sr.No | Location | Meter | Previous Reading | 2026-03-01 | 2026-03-02 | 2026-03-03 | 2026-03-04 | 2026-03-05 | 2026-03-06 | 2026-03-07 | 2026-03-08 | 2026-03-09 | 2026-03-10 | 2026-03-11 | 2026-03-12 | 2026-03-13 | 2026-03-14 | 2026-03-15 | 2026-03-16 | 2026-03-17 | 2026-03-18 | 2026-03-19 | 2026-03-20 | 2026-03-21 | 2026-03-22 | 2026-03-23 | 2026-03-24 | 2026-03-25 | 2026-03-26 | 2026-03-27 | 2026-03-28 | 2026-03-29 | 2026-03-30 | 2026-03-31 | Consumption
|  |  |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170 | 2216 | 2216 | 2241 | 2241 | 2241 | 2272 | 2297 | 2297 | 2297 | 2322 | 2329 | 2336 | 2344 | 2370 | 2370 | 2370 | 2382 | 2407 | 2437 | 2437 | 2437 | 2437 | 2437 | 2459 | 2485
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170

## Feb-2026
FEB- 2026
Sr.No | Location | Meter | Previous Reading | 2026-02-01 | 2026-02-02 | 2026-02-03 | 2026-02-04 | 2026-02-05 | 2026-02-06 | 2026-02-07 | 2026-02-08 | 2026-02-09 | 2026-02-10 | 2026-02-11 | 2026-02-12 | 2026-02-13 | 2026-02-14 | 2026-02-15 | 2026-02-16 | 2026-02-17 | 2026-02-18 | 2026-02-19 | 2026-02-20 | 2026-02-21 | 2026-02-22 | 2026-02-23 | 2026-02-24 | 2026-02-25 | 2026-02-26 | 2026-02-27 | 2026-02-28 | Consumption
|  |  |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 174539 | 174831 | 175100 | 175349 | 175600 | 175858 | 176115 | 176323 | 176539 | 176807 | 177067 | 177320 | 177586 | 177836 | 178053 | 178233 | 178494 | 178759 | 179010 | 179260 | 179511 | 179718 | 179917 | 180174 | 180449 | 180698 | 180957 | 181217 | 181312
|  | DG | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 253441 | 253820 | 254213 | 254575 | 254949 | 255315 | 255684 | 255965 | 256254 | 256648 | 257026 | 257397 | 257784 | 258148 | 258434 | 258676 | 259048 | 259431 | 259794 | 260155 | 260518 | 260797 | 261061 | 261430 | 261827 | 262190 | 262566 | 262852 | 263065
|  | DG | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 131062 | 131292 | 131506 | 131800 | 132049 | 132289 | 132537 | 132691 | 132848 | 133099 | 133343 | 133586 | 133839 | 134080 | 134244 | 134379 | 134623 | 134878 | 135126 | 135373 | 135615 | 135780 | 135920 | 136179 | 136447 | 136692 | 136933 | 137176 | 137256
|  | DG | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280
6 | 3F | SL No 540430038646 (EB Unit) | 147456 | 147615 | 147867 | 148133 | 148380 | 148664 | 148922 | 149040 | 149120 | 149390 | 149641 | 149911 | 150175 | 150444 | 150560 | 150651 | 150870 | 151209 | 151466 | 151734 | 151987 | 152116 | 152200 | 152455 | 152730 | 153003 | 153256 | 153524 | 153569
|  | DG | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265
7 | 3F | SL No 540430038843 (EB Unit) | 486295 | 487006 | 487827 | 488588 | 489417 | 490208 | 491030 | 491662 | 492129 | 492933 | 493745 | 494531 | 495362 | 496164 | 496807 | 497268 | 498051 | 498873 | 499668 | 500480 | 501274 | 501909 | 502389 | 502980 | 504032 | 504812 | 505620 | 506457 | 506717
|  | DG | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614
8 | 3F | SL No 540430038848 (EB Unit) | 94542 | 94674 | 94791 | 94887 | 95003 | 95103 | 95225 | 95316 | 95417 | 95528 | 95644 | 95755 | 95884 | 95990 | 96095 | 96177 | 96294 | 96410 | 96529 | 96645 | 96765 | 96868 | 96973 | 97076 | 97205 | 97321 | 97444 | 97565 | 97629
|  | DG | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214
1 | 3F | AHU1 | 49293 | 49373 | 49489 | 49646 | 49829 | 50011 | 50169 | 50274 | 50274 | 50419 | 50572 | 50735 | 50900 | 51051 | 51085 | 51085 | 51211 | 51364 | 51495 | 51627 | 51788 | 51921 | 51921 | 52070 | 52230 | 52369 | 52505 | 52644 | 52703
|  | DG | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923 | 1923
2 | 3F | AHU2 | 52906 | 52988 | 53112 | 53241 | 53362 | 53502 | 53621 | 53714 | 53714 | 53872 | 54010 | 54152 | 54303 | 54457 | 54497 | 54497 | 54661 | 54850 | 55006 | 55145 | 55261 | 55349 | 55360 | 55461 | 55540 | 55610 | 55683 | 55771 | 55794
|  | DG | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911 | 1911
3 | 3F | AHU3 | 65921 | 65977 | 66090 | 66207 | 66322 | 66446 | 66534 | 66615 | 66615 | 66733 | 66839 | 66938 | 67051 | 67180 | 67181 | 67181 | 67335 | 67479 | 67590 | 67716 | 67841 | 67948 | 67949 | 68039 | 68148 | 68241 | 68353 | 68455 | 68469
|  | DG | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068 | 2068
4 | 3F | AHU4 | 43502 | 43557 | 43598 | 43696 | 43803 | 43914 | 43957 | 44006 | 44006 | 44095 | 44201 | 44309 | 44406 | 44506 | 44506 | 44506 | 44623 | 44764 | 44906 | 45012 | 45125 | 45159 | 45159 | 45198 | 45248 | 45285 | 45326 | 45366 | 45373
|  | DG | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788 | 1788
1 | 3F | AHU1 - BTU | 394335 | 394529 | 394780 | 395172 | 395438 | 395746 | 396130 | 396382 | 396384 | 396771 | 397175 | 397646 | 398105 | 398540 | 398616 | 398616 | 399031 | 399519 | 399977 | 400328 | 400709 | 400993 | 400993 | 401453 | 402025 | 402476 | 402844 | 403259 | 403490
2 | 3F | AHU2 - BTU | 370360 | 370538 | 370818 | 371159 | 371466 | 371768 | 372097 | 372301 | 372301 | 372742 | 373142 | 373455 | 373794 | 374169 | 374287 | 374587 | 374770 | 375241 | 375708 | 376115 | 376469 | 376760 | 376780 | 377287 | 377775 | 378160 | 378522 | 378872 | 378984
3 | 3F | AHU3 - BTU | 398878 | 399037 | 399232 | 399521 | 399806 | 400112 | 400363 | 400496 | 400496 | 400733 | 401009 | 401214 | 401550 | 401891 | 401892 | 401892 | 402318 | 402694 | 403135 | 403387 | 403763 | 404016 | 404016 | 404439 | 404980 | 405523 | 405908 | 406266 | 406367
4 | 3F | AHU4 - BTU | 428437 | 428733 | 429192 | 429704 | 430200 | 430748 | 431322 | 431625 | 431660 | 432274 | 432850 | 433422 | 433751 | 434237 | 434311 | 434311 | 434830 | 435186 | 435764 | 436495 | 437347 | 437676 | 437711 | 438234 | 438931 | 439476 | 439926 | 440273 | 440357
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter |  | 2026-02-01: 2026-02-01 | Consumption
|  |  |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time |  | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [30 empty] | EB
3 | 3F | AHU3 | [30 empty] | AHU
|  | DG | [30 empty] | BTU
4 | 3F | AHU4 | [30 empty] | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption
FEB- 2026 EV METER READING
Sr.No | Location | Meter | Previous Reading | 2026-02-01 | 2026-02-02 | 2026-02-03 | 2026-02-04 | 2026-02-05 | 2026-02-06 | 2026-02-07 | 2026-02-08 | 2026-02-09 | 2026-02-10 | 2026-02-11 | 2026-02-12 | 2026-02-13 | 2026-02-14 | 2026-02-15 | 2026-02-16 | 2026-02-17 | 2026-02-18 | 2026-02-19 | 2026-02-20 | 2026-02-21 | 2026-02-22 | 2026-02-23 | 2026-02-24 | 2026-02-25 | 2026-02-26 | 2026-02-27 | 2026-02-28
|  |  |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170 | 1942 | 1942 | 1953 | 1978 | 1978 | 1998 | 1998 | 1998 | 1998 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2017 | 2041 | 2066 | 2081 | 2107 | 2128 | 2128 | 2128 | 2128 | 2152 | 2176 | 2202 | 2216 | 2216
Sr.No | Location | Meter | [29 empty] | Consumption
|  |  |  | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170

## Jan-2026
JAN- 2026
Sr.No | Location | Meter | Previous Reading | 2026-01-01 | 2026-01-02 | 2026-01-03 | 2026-01-04 | 2026-01-05 | 2026-01-06 | 2026-01-07 | 2026-01-08 | 2026-01-09 | 2026-01-10 | 2026-01-11 | 2026-01-12 | 2026-01-13 | 2026-01-14 | 2026-01-15 | 2026-01-16 | 2026-01-17 | 2026-01-18 | 2026-01-19 | 2026-01-20 | 2026-01-21 | 2026-01-22 | 2026-01-23 | 2026-01-24 | 2026-01-25 | 2026-01-26 | 2026-01-27 | 2026-01-28 | 2026-01-29 | 2026-01-30 | 2026-01-31 | Consumption
|  |  |  | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 167218 | 167542 | 167774 | 167980 | 168197 | 168430 | 168686 | 168939 | 169174 | 169417 | 169628 | 169835 | 170093 | 170347 | 170594 | 170843 | 171080 | 171283 | 171505 | 171746 | 172018 | 172271 | 172545 | 172791 | 173012 | 173195 | 173405 | 173667 | 173900 | 174192 | 174429 | 174539
|  | DG | 4281 | 4281 | 4281 | 4281 | 4281 | 4281 | 4281 | 4281 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283 | 4283
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 243129 | 243575 | 243896 | 244174 | 244461 | 244802 | 245170 | 245445 | 245869 | 246216 | 246504 | 246779 | 247152 | 247513 | 247865 | 248225 | 248562 | 248834 | 249125 | 249483 | 249876 | 250247 | 250652 | 250997 | 251294 | 251536 | 251816 | 252193 | 252566 | 252957 | 253301 | 253441
|  | DG | 6407 | 6407 | 6407 | 6407 | 6407 | 6407 | 6407 | 6407 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410 | 6410
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 124335 | 124585 | 124796 | 124964 | 125134 | 125372 | 125627 | 125881 | 126122 | 126356 | 126518 | 126682 | 126945 | 127193 | 127434 | 127675 | 127903 | 128064 | 128229 | 128471 | 128732 | 128989 | 129261 | 129494 | 129664 | 129801 | 129932 | 130183 | 130438 | 130712 | 130970 | 131062
|  | DG | 3278 | 3278 | 3278 | 3278 | 3278 | 3278 | 3278 | 3278 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280 | 3280
6 | 3F | SL No 540430038646 (EB Unit) | 141339 | 141512 | 141739 | 141823 | 141909 | 142150 | 142405 | 142666 | 142916 | 143154 | 143265 | 143347 | 143622 | 143821 | 144124 | 144356 | 144588 | 144670 | 144766 | 145026 | 145298 | 145555 | 145854 | 146102 | 146207 | 146277 | 146364 | 146620 | 146903 | 147141 | 147399 | 147456
|  | DG | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265 | 4265
7 | 3F | SL No 540430038843 (EB Unit) | 464366 | 465312 | 466032 | 466646 | 467230 | 467963 | 468778 | 469606 | 470375 | 471146 | 471740 | 472262 | 473083 | 473861 | 474664 | 475449 | 476207 | 476751 | 477288 | 478043 | 478895 | 479694 | 480556 | 481336 | 481908 | 482373 | 482788 | 483581 | 483980 | 485211 | 485976 | 486295
|  | DG | 11607 | 11607 | 11607 | 11607 | 11607 | 11607 | 11607 | 11607 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614 | 11614
8 | 3F | SL No 540430038848 (EB Unit) | 91210 | 91368 | 91476 | 91575 | 91664 | 91769 | 91874 | 92000 | 92104 | 92220 | 92312 | 92403 | 92513 | 92637 | 92742 | 92855 | 92959 | 93061 | 93157 | 93276 | 93391 | 93515 | 93639 | 93756 | 93851 | 93931 | 94016 | 94138 | 94253 | 94373 | 94479 | 94542
|  | DG | 2213 | 2213 | 2213 | 2213 | 2213 | 2213 | 2213 | 2213 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214 | 2214
1 | 3F | AHU1 | 45884 | 45956 | 46034 | 46035 | 46036 | 46168 | 46326 | 46500 | 46669 | 46854 | 46988 | 46988 | 47119 | 47283 | 47431 | 47533 | 47647 | 47663 | 47663 | 47817 | 47993 | 48183 | 48377 | 48545 | 48550 | 48591 | 48591 | 48741 | 48911 | 49041 | 49203 | 49293
|  | DG | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1923
2 | 3F | AHU2 | 49831 | 49898 | 49975 | 49975 | 49976 | 50106 | 50212 | 50337 | 50439 | 50561 | 50696 | 50696 | 50817 | 50933 | 51051 | 51187 | 51319 | 51344 | 51344 | 51515 | 51678 | 51832 | 51980 | 52160 | 52169 | 52169 | 52169 | 52358 | 52550 | 52686 | 52866 | 52906
|  | DG | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1911
3 | 3F | AHU3 | 61348 | 61462 | 61643 | 61826 | 62019 | 62207 | 62379 | 62571 | 62755 | 62940 | 63129 | 63316 | 63513 | 63698 | 63883 | 64023 | 64218 | 64320 | 64320 | 64476 | 64662 | 64838 | 65003 | 65158 | 65332 | 65380 | 65380 | 65510 | 65667 | 65778 | 65894 | 65921
|  | DG | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2068
4 | 3F | AHU4 | 41608 | 41614 | 41801 | 41801 | 41803 | 41944 | 42061 | 42189 | 42289 | 42385 | 42438 | 42438 | 42517 | 42592 | 42660 | 42767 | 42819 | 42819 | 42819 | 42952 | 43006 | 43051 | 43093 | 43139 | 43139 | 43139 | 43139 | 43253 | 43300 | 43397 | 43502 | 43502
|  | DG | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1788
1 | 3F | AHU1 - BTU | 388786 | 388786 | 388989 | 388997 | 388997 | 389234 | 389479 | 389717 | 389974 | 390145 | 390320 | 390320 | 390507 | 390801 | 391035 | 391137 | 391284 | 391340 | 391340 | 391655 | 392070 | 392394 | 392730 | 392957 | 393032 | 393033 | 393033 | 393302 | 393652 | 393962 | 394254 | 394335
2 | 3F | AHU2 - BTU | 364801 | 364801 | 364942 | 364942 | 364942 | 365152 | 365356 | 365548 | 365752 | 365874 | 366053 | 366084 | 366288 | 366462 | 366716 | 366938 | 367126 | 367174 | 367174 | 367527 | 367906 | 367906 | 368686 | 368931 | 369007 | 369007 | 369007 | 369310 | 369718 | 369986 | 370271 | 370360
3 | 3F | AHU3 - BTU | 391409 | 391409 | 391825 | 392013 | 392117 | 392377 | 392724 | 393049 | 393382 | 393636 | 393926 | 394110 | 394364 | 394683 | 395014 | 395146 | 395378 | 395602 | 395602 | 395861 | 396223 | 396901 | 396936 | 397229 | 397522 | 397668 | 397668 | 397838 | 398215 | 398464 | 398786 | 398878
4 | 3F | AHU4 - BTU | 421615 | 421615 | 421903 | 421937 | 421937 | 422256 | 422450 | 422666 | 422851 | 423008 | 423199 | 423243 | 423479 | 423759 | 423963 | 424174 | 424406 | 424463 | 424463 | 424998 | 425394 | 425852 | 426330 | 426609 | 426674 | 426688 | 426688 | 427118 | 427494 | 427900 | 428345 | 428437
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter |  | 2026-01-01: 2026-01-01; 2026-01-31: 2025-12-31 | Consumption
|  |  |  | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time |  | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [33 empty] | EB
3 | 3F | AHU3 | [33 empty] | AHU
|  | DG | [33 empty] | BTU
4 | 3F | AHU4 | [33 empty] | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption
JAN- 2026 EV METER READING
Sr.No | Location | Meter | Previous Reading | 2026-01-01 | 2026-01-02 | 2026-01-03 | 2026-01-04 | 2026-01-05 | 2026-01-06 | 2026-01-07 | 2026-01-08 | 2026-01-09 | 2026-01-10 | 2026-01-11 | 2026-01-12 | 2026-01-13 | 2026-01-14 | 2026-01-15 | 2026-01-16 | 2026-01-17 | 2026-01-18 | 2026-01-19 | 2026-01-20 | 2026-01-21 | 2026-01-22 | 2026-01-23 | 2026-01-24 | 2026-01-25 | 2026-01-26 | 2026-01-27 | 2026-01-28 | 2026-01-29 | 2026-01-30 | 2026-01-31
|  |  |  | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170 | 1703 | 1703 | 1703 | 1703 | 1703 | 1724 | 1750 | 1774 | 1797 | 1808 | 1808 | 1808 | 1808 | 1833 | 1833 | 1846 | 1868 | 1868 | 1868 | 1868 | 1875 | 1903 | 1918 | 1918 | 1918 | 1918 | 1918 | 1918 | 1918 | 1942 | 1942 | 1942
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170

## Dec-25
DEC- 2025
Sr.No | Location | Meter | Previous Reading | 2025-12-01 | 2025-12-02 | 2025-12-03 | 2025-12-04 | 2025-12-05 | 2025-12-06 | 2025-12-07 | 2025-12-08 | 2025-12-09 | 2025-12-10 | 2025-12-11 | 2025-12-12 | 2025-12-13 | 2025-12-14 | 2025-12-15 | 2025-12-16 | 2025-12-17 | 2025-12-18 | 2025-12-19 | 2025-12-20 | 2025-12-21 | 2025-12-22 | 2025-12-23 | 2025-12-24 | 2025-12-25 | 2025-12-26 | 2025-12-27 | 2025-12-28 | 2025-12-29 | 2025-12-30 | 2025-12-31 | Consumption
|  |  |  | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 160014 | 2025-12-31: 167218 | 7204
|  | DG | 4279 | 2025-12-31: 4281
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 2025-12-31: 1956
|  | DG | 28.6 | 2025-12-31: 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 232941 | 2025-12-31: 243129 | 10188
|  | DG | 6406 | 2025-12-31: 6407
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 2025-12-31: 0
|  | DG | 0 | 2025-12-31: 0
5 | 3F | SL No 540430038849 (EB Unit) | 117671 | 2025-12-31: 124335
|  | DG | 3277 | 2025-12-31: 3278
6 | 3F | SL No 540430038646 (EB Unit) | 135314 | 2025-12-31: 141339 | 6664
|  | DG | 4262 | 2025-12-31: 4262
7 | 3F | SL No 540430038843 (EB Unit) | 442589 | 2025-12-31: 464366 | 21777
|  | DG | 11604 | 2025-12-31: 11607
8 | 3F | SL No 540430038848 (EB Unit) | 87969 | 2025-12-31: 91210 | 3241
|  | DG | 2212 | 2025-12-31: 2213
1 | 3F | AHU1 | 43073 | 2025-12-31: 45884 | 2811
|  | DG | 1921 | 2025-12-31: 1921
2 | 3F | AHU2 | 47109 | 2025-12-31: 49831 | 2722
|  | DG | 1909 | 2025-12-31: 1909
3 | 3F | AHU3 | 55482 | 2025-12-31: 61348 | 5866
|  | DG | 2065 | 2025-12-31: 2065
4 | 3F | AHU4 | 39556 | 2025-12-31: 41608 | 2052
|  | DG | 1786 | 2025-12-31: 1786
1 | 3F | AHU1 - BTU | 381319 | 2025-12-31: 388786 | 7467
2 | 3F | AHU2 - BTU | 358128 | 2025-12-31: 364801 | 6673
3 | 3F | AHU3 - BTU | 379512 | 2025-12-31: 391409 | 11897
4 | 3F | AHU4 - BTU | 412336 | 2025-12-31: 421615 | 9279
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter |  | 2025-12-31: 2025-12-31 | Consumption
|  |  |  | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time |  | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [33 empty] | EB
3 | 3F | AHU3 | [33 empty] | AHU
|  | DG | [33 empty] | BTU
4 | 3F | AHU4 | [33 empty] | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption
Nove- 2025 EV METER READING
Sr.No | Location | Meter | Previous Reading | 2025-12-01 | 2025-12-02 | 2025-12-03 | 2025-12-04 | 2025-12-05 | 2025-12-06 | 2025-12-07 | 2025-12-08 | 2025-12-09 | 2025-12-10 | 2025-12-11 | 2025-12-12 | 2025-12-13 | 2025-12-14 | 2025-12-15 | 2025-12-16 | 2025-12-17 | 2025-12-18 | 2025-12-19 | 2025-12-20 | 2025-12-21 | 2025-12-22 | 2025-12-23 | 2025-12-24 | 2025-12-25 | 2025-12-26 | 2025-12-27 | 2025-12-28 | 2025-12-29 | 2025-12-30 | 2025-12-31
|  |  |  | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170 | 1528 | 1550 | 1550 | 1562 | 1578 | 1600 | 1600 | 1600 | 1620 | 1620 | 1645 | 1671 | 1682 | 1682 | 1682 | 1682 | 1682 | 1682 | 1694 | 1694 | 1694 | 1694 | 1694 | 1694 | 1703 | 1703 | 1703 | 1703 | 1703 | 1703 | 1703 | 1703
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170

## Nov-25
Nov- 2025
Sr.No | Location | Meter | Previous Reading | 2025-11-01 | 2025-11-02 | 2025-11-03 | 2025-11-04 | 2025-11-05 | 2025-11-06 | 2025-11-07 | 2025-11-08 | 2025-11-09 | 2025-11-10 | 2025-11-11 | 2025-11-12 | 2025-11-13 | 2025-11-14 | 2025-11-15 | 2025-11-16 | 2025-11-17 | 2025-11-18 | 2025-11-19 | 2025-11-20 | 2025-11-21 | 2025-11-22 | 2025-11-23 | 2025-11-24 | 2025-11-25 | 2025-11-26 | 2025-11-27 | 2025-11-28 | 2025-11-29 | 2025-11-30 | Consumption
|  |  |  | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 152751 | 152969 | 153180 | 153462 | 153738 | 153964 | 154249 | 154547 | 154735 | 154928 | 155230 | 155506 | 155775 | 156033 | 156288 | 156514 | 156727 | 156979 | 157237 | 157497 | 157752 | 157997 | 158215 | 158425 | 158680 | 158934 | 159188 | 159441 | 159689 | 159902 | 160014
|  | DG | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 222574 | 222865 | 223147 | 223568 | 223979 | 224288 | 224724 | 225163 | 225414 | 225695 | 226122 | 226532 | 226924 | 227301 | 227669 | 227977 | 228262 | 228629 | 229004 | 229387 | 229744 | 230108 | 230400 | 230685 | 231053 | 231420 | 231787 | 232148 | 232503 | 232792 | 232941
|  | DG | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406 | 6406
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 110988 | 111165 | 111338 | 111626 | 111905 | 112108 | 112408 | 112694 | 112832 | 112996 | 113278 | 113540 | 113800 | 114045 | 114277 | 114443 | 114603 | 114850 | 115103 | 115366 | 115609 | 115848 | 116019 | 116177 | 116426 | 116670 | 116922 | 117173 | 117418 | 117588 | 117671
|  | DG | 3276 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277 | 3277
6 | 3F | SL No 540430038646 (EB Unit) | 129622 | 129731 | 129821 | 130068 | 130324 | 130444 | 130717 | 130967 | 131059 | 131129 | 131383 | 131622 | 131875 | 132097 | 132338 | 132457 | 132544 | 132768 | 133023 | 133255 | 133493 | 133735 | 133863 | 133939 | 134195 | 134414 | 134663 | 134904 | 135144 | 135248 | 135314
|  | DG | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262 | 4262
7 | 3F | SL No 540430038843 (EB Unit) | 421416 | 422031 | 422568 | 423347 | 424139 | 424789 | 425565 | 426414 | 426862 | 427430 | 428205 | 429030 | 429833 | 430631 | 431414 | 432104 | 432614 | 433383 | 434195 | 434998 | 435812 | 436575 | 436998 | 437769 | 438561 | 439364 | 440174 | 440983 | 441784 | 442348 | 442589
|  | DG | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604 | 11604
8 | 3F | SL No 540430038848 (EB Unit) | 84560 | 84691 | 84800 | 84942 | 85060 | 85170 | 85293 | 85430 | 85527 | 85638 | 85708 | 85875 | 85980 | 86100 | 86204 | 86323 | 86424 | 86538 | 86639 | 86766 | 86865 | 87007 | 87115 | 87115 | 87225 | 87456 | 87553 | 87672 | 87776 | 87878 | 87969
|  | DG | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212
1 | 3F | AHU1 | 40295 | 40370 | 40371 | 40452 | 40555 | 40656 | 40755 | 40863 | 40903 | 40904 | 40998 | 41092 | 41206 | 41325 | 41453 | 41547 | 41561 | 41673 | 41833 | 41973 | 42113 | 42249 | 42369 | 42369 | 42478 | 42622 | 42730 | 42891 | 43025 | 43073 | 43073
|  | DG | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921
2 | 3F | AHU2 | 44440 | 44514 | 44515 | 44615 | 44748 | 44830 | 44942 | 45089 | 45101 | 45102 | 45186 | 45281 | 45407 | 45519 | 45640 | 45759 | 45779 | 45908 | 46046 | 46184 | 46300 | 46429 | 46492 | 46492 | 46606 | 46726 | 46837 | 46960 | 47098 | 47109 | 47109
|  | DG | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909
3 | 3F | AHU3 | 49792 | 49957 | 50177 | 50393 | 50605 | 50807 | 51036 | 51260 | 51449 | 51460 | 51618 | 51772 | 51963 | 52158 | 52357 | 52555 | 52567 | 52955 | 53163 | 53359 | 53565 | 53760 | 53965 | 53965 | 54364 | 54564 | 54762 | 54963 | 55165 | 55365 | 55482
|  | DG | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065
4 | 3F | AHU4 | 37838 | 37877 | 37877 | 37957 | 38038 | 38094 | 38160 | 38220 | 38221 | 38221 | 38298 | 38361 | 38437 | 38513 | 38591 | 38641 | 38660 | 38742 | 38814 | 38901 | 38975 | 39062 | 39134 | 39134 | 39217 | 39303 | 39379 | 39476 | 39552 | 39552 | 39556
|  | DG | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786
1 | 3F | AHU1 - BTU | 372385 | 372886 | 372886 | 373331 | 373790 | 374233 | 374725 | 375086 | 375223 | 375223 | 375666 | 376119 | 376497 | 376911 | 377195 | 377392 | 377418 | 377793 | 378097 | 378522 | 378905 | 379169 | 379493 | 379496 | 379859 | 380258 | 380634 | 380935 | 381253 | 381318 | 381319
2 | 3F | AHU2 - BTU | 349743 | 350195 | 350195 | 350689 | 351161 | 351360 | 351750 | 352211 | 352268 | 352268 | 352645 | 353051 | 353410 | 353738 | 354109 | 354411 | 354446 | 354833 | 355204 | 355568 | 355884 | 356222 | 356455 | 356455 | 356807 | 357160 | 357468 | 357754 | 358060 | 358128 | 358128
3 | 3F | AHU3 - BTU | 366099 | 366730 | 367031 | 367753 | 368219 | 368592 | 369097 | 369675 | 370025 | 370025 | 370612 | 371161 | 371632 | 372130 | 372705 | 373070 | 373402 | 373884 | 374412 | 374871 | 375368 | 375822 | 376345 | 376724 | 377212 | 377772 | 378257 | 378386 | 379011 | 379349 | 379512
4 | 3F | AHU4 - BTU | 399618 | 400108 | 400166 | 400862 | 401600 | 402142 | 402804 | 403363 | 403409 | 403409 | 404093 | 404765 | 405295 | 405869 | 406369 | 406677 | 406751 | 407304 | 407704 | 408191 | 408645 | 409153 | 409536 | 409580 | 410125 | 410649 | 411141 | 411634 | 412243 | 412307 | 412336
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [31 empty] | Consumption
|  |  |  | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [32 empty] | EB
3 | 3F | AHU3 | [32 empty] | AHU
|  | DG | [32 empty] | BTU
4 | 3F | AHU4 | [32 empty] | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption
Nove- 2025 EV METER READING
Sr.No | Location | Meter | Previous Reading | 2025-11-01 | 2025-11-02 | 2025-11-03 | 2025-11-04 | 2025-11-05 | 2025-11-06 | 2025-11-07 | 2025-11-08 | 2025-11-09 | 2025-11-10 | 2025-11-11 | 2025-11-12 | 2025-11-13 | 2025-11-14 | 2025-11-15 | 2025-11-16 | 2025-11-17 | 2025-11-18 | 2025-11-19 | 2025-11-20 | 2025-11-21 | 2025-11-22 | 2025-11-23 | 2025-11-24 | 2025-11-25 | 2025-11-26 | 2025-11-27 | 2025-11-28 | 2025-11-29 | 2025-11-30
|  |  |  | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170 | 1378 | 1378 | 1378 | 1378 | 1421 | 1421 | 1441 | 1462 | 1462 | 1462 | 1462 | 1478 | 1489 | 1489 | 1489 | 1489 | 1489 | 1489 | 1489 | 1489 | 1489 | 1489 | 1489 | 1489 | 1489 | 1495 | 1495 | 1508 | 1528 | 1528 | 1528
Sr.No | Location | Meter | [31 empty] | Consumption
|  |  |  | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | Basement:-2 | Liberty-170

## Oct-25
Oct- 2025
Sr.No | Location | Meter | Previous Reading | 2025-10-01 | 2025-10-02 | 2025-10-03 | 2025-10-04 | 2025-10-05 | 2025-10-06 | 2025-10-07 | 2025-10-08 | 2025-10-09 | 2025-10-10 | 2025-10-11 | 2025-10-12 | 2025-10-13 | 2025-10-14 | 2025-10-15 | 2025-10-16 | 2025-10-17 | 2025-10-18 | 2025-10-19 | 2025-10-20 | 2025-10-21 | 2025-10-22 | 2025-10-23 | 2025-10-24 | 2025-10-25 | 2025-10-26 | 2025-10-27 | 2025-10-28 | 2025-10-29 | 2025-10-30 | 2025-10-31 | Consumption
|  |  |  | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 145003 | 145380 | 145582 | 145837 | 146045 | 146251 | 146542 | 146814 | 147098 | 147378 | 147641 | 147850 | 148069 | 148347 | 148623 | 148901 | 149167 | 149420 | 149625 | 149827 | 150038 | 150256 | 150483 | 150725 | 150991 | 151181 | 151397 | 151663 | 151935 | 152207 | 152491 | 152751
|  | DG | 4278 | 4278 | 4278 | 4278 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279 | 4279
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 211463 | 212016 | 212278 | 212658 | 212936 | 213210 | 213642 | 214054 | 214464 | 214911 | 215286 | 215584 | 215864 | 216279 | 216692 | 217106 | 217491 | 217828 | 218135 | 218402 | 218686 | 218979 | 219296 | 219638 | 220018 | 220273 | 220520 | 220956 | 221359 | 221767 | 222187 | 222574
|  | DG | 6403 | 6403 | 6403 | 6403 | 6403 | 6403 | 6403 | 6403 | 6403 | 6403 | 6403 | 6403 | 6403 | 6403 | 6403 | 6403 | 6405 | 6405 | 6405 | 6405 | 6405 | 6405 | 6405 | 6405 | 6405 | 6405 | 6405 | 6405 | 6405 | 6405 | 6406 | 6406
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 104459 | 104792 | 104929 | 105147 | 105297 | 105442 | 105707 | 105955 | 106210 | 106473 | 106696 | 106845 | 106983 | 107229 | 107479 | 107738 | 107978 | 108208 | 108355 | 108499 | 108637 | 108816 | 109011 | 109215 | 109445 | 109578 | 109725 | 109968 | 110218 | 110470 | 110739 | 110988
|  | DG | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276 | 3276
6 | 3F | SL No 540430038646 (EB Unit) | 123060 | 123460 | 123547 | 123812 | 123920 | 124031 | 124031 | 124555 | 124810 | 125094 | 125353 | 125490 | 125597 | 125889 | 126150 | 126405 | 126683 | 126925 | 127028 | 127132 | 127222 | 127437 | 127648 | 127878 | 128113 | 128215 | 128306 | 128570 | 128812 | 129083 | 129343 | 129622
|  | DG | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4261 | 4262
7 | 3F | SL No 540430038843 (EB Unit) | 399411 | 400558 | 400981 | 401685 | 402303 | 402796 | 402796 | 404417 | 405216 | 406012 | 406813 | 407491 | 408013 | 408776 | 409608 | 410435 | 411254 | 412070 | 412692 | 413201 | 413562 | 414175 | 414894 | 415672 | 416483 | 416939 | 417442 | 418206 | 419018 | 419803 | 420649 | 421416
|  | DG | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11600 | 11604
8 | 3F | SL No 540430038848 (EB Unit) | 80798 | 80959 | 81083 | 81083 | 81341 | 81462 | 81609 | 81726 | 81852 | 81926 | 82100 | 82207 | 82330 | 82447 | 82577 | 82694 | 82825 | 82941 | 83052 | 83150 | 83272 | 83387 | 83516 | 83618 | 83755 | 83850 | 83969 | 84088 | 84220 | 84220 | 84453 | 84560
|  | DG | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212 | 2212
1 | 3F | AHU1 | 37637 | 37804 | 37804 | 37908 | 37977 | 37977 | 38068 | 38207 | 38324 | 38454 | 38593 | 38709 | 38709 | 38794 | 38920 | 39056 | 39188 | 39313 | 39357 | 39357 | 39357 | 39458 | 39541 | 39633 | 39757 | 39788 | 39788 | 39908 | 40037 | 40135 | 40230 | 40295
|  | DG | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921 | 1921
2 | 3F | AHU2 | 41922 | 42102 | 42102 | 42328 | 42260 | 42260 | 42356 | 42452 | 42560 | 42650 | 42776 | 42865 | 42865 | 42961 | 43069 | 43214 | 43329 | 43444 | 43459 | 43459 | 43459 | 43577 | 43669 | 43771 | 43892 | 43901 | 43901 | 44040 | 44199 | 44297 | 44391 | 44440
|  | DG | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909 | 1909
3 | 3F | AHU3 | 45953 | 46178 | 46178 | 46328 | 46394 | 46399 | 46538 | 46734 | 46912 | 47080 | 47244 | 47329 | 47329 | 47446 | 47607 | 47774 | 47931 | 48089 | 48194 | 48194 | 48194 | 48310 | 48422 | 48582 | 48752 | 48820 | 48820 | 48991 | 49201 | 49416 | 49643 | 49792
|  | DG | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065 | 2065
4 | 3F | AHU4 | 35709 | 35863 | 35863 | 35963 | 36022 | 36022 | 36133 | 36233 | 36324 | 36416 | 36504 | 36523 | 36523 | 36621 | 36734 | 36843 | 36955 | 37066 | 37066 | 37066 | 37066 | 37137 | 37234 | 37318 | 37420 | 37428 | 37428 | 37546 | 37640 | 37719 | 37793 | 37838
|  | DG | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786 | 1786
1 | 3F | AHU1 - BTU | 360811 | 361428 | 361428 | 362050 | 362395 | 362395 | 362906 | 363387 | 363885 | 364404 | 364850 | 365202 | 365202 | 365723 | 366347 | 366938 | 367435 | 367859 | 368024 | 368024 | 368024 | 368581 | 369143 | 369509 | 369894 | 370067 | 370067 | 370571 | 371145 | 371693 | 372191 | 372385
2 | 3F | AHU2 - BTU | 338439 | 339141 | 339141 | 339876 | 340409 | 340409 | 341046 | 341566 | 342141 | 342540 | 342986 | 343310 | 343310 | 343864 | 344373 | 344848 | 345330 | 345794 | 345863 | 345863 | 345863 | 346481 | 346953 | 347300 | 347666 | 347745 | 347745 | 348285 | 348700 | 349094 | 349525 | 349743
3 | 3F | AHU3 - BTU | 353063 | 353933 | 353933 | 354542 | 354967 | 354967 | 355610 | 356169 | 356832 | 357358 | 357839 | 358170 | 358170 | 358820 | 359331 | 359829 | 360352 | 360834 | 361089 | 361089 | 361089 | 361765 | 362218 | 362697 | 363044 | 363323 | 363323 | 363822 | 364337 | 365030 | 365724 | 366099
4 | 3F | AHU4 - BTU | 381662 | 382755 | 382755 | 383753 | 384318 | 384318 | 385206 | 386191 | 387042 | 387795 | 388638 | 388900 | 388900 | 389712 | 390569 | 391407 | 392276 | 393114 | 393223 | 393223 | 393223 | 393958 | 394651 | 395357 | 395977 | 396174 | 396174 | 396983 | 397731 | 398516 | 399217 | 399618
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter |  | 2025-10-31: 2025-10-31 | Consumption
|  |  |  | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time |  | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [33 empty] | EB
3 | 3F | AHU3 | [33 empty] | AHU
|  | DG | [33 empty] | BTU
4 | 3F | AHU4 | [33 empty] | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## Sep-2025
SEP- 2025
Sr.No | Location | Meter | Previous Reading | 2025-09-01 | 2025-09-02 | 2025-09-03 | 2025-09-04 | 2025-09-05 | 2025-09-06 | 2025-09-07 | 2025-09-08 | 2025-09-09 | 2025-09-10 | 2025-09-11 | 2025-09-12 | 2025-09-13 | 2025-09-14 | 2025-09-15 | 2025-09-16 | 2025-09-17 | 2025-09-18 | 2025-09-19 | 2025-09-20 | 2025-09-21 | 2025-09-22 | 2025-09-23 | 2025-09-24 | 2025-09-25 | 2025-09-26 | 2025-09-27 | 2025-09-28 | 2025-09-29 | 2025-09-30 | Consumption
|  |  |  | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 137403 | 137778 | 137998 | 138285 | 138563 | 138839 | 139050 | 139264 | 139537 | 139823 | 140115 | 140390 | 140672 | 140882 | 141098 | 141289 | 141563 | 141838 | 142093 | 142385 | 142594 | 142804 | 143073 | 143346 | 143628 | 143911 | 144177 | 144385 | 144583 | 144860 | 145003
|  | DG | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4258 | 4258 | 4258 | 4258 | 4258 | 4258 | 4258 | 4258 | 4258 | 4258 | 4258 | 4258 | 4268 | 4278 | 4278 | 4278
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 200443 | 200988 | 201316 | 201714 | 202131 | 202536 | 202817 | 203103 | 203511 | 203942 | 204378 | 204795 | 205218 | 205500 | 205787 | 206065 | 206473 | 206888 | 207301 | 207695 | 207981 | 208255 | 208659 | 209065 | 209482 | 209903 | 210296 | 210578 | 210844 | 211255 | 211463
|  | DG | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6375 | 6375 | 6375 | 6375 | 6375 | 6375 | 6375 | 6375 | 6375 | 6375 | 6375 | 6375 | 6389 | 6403 | 6403 | 6403
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 97925 | 98247 | 98452 | 98667 | 98930 | 99184 | 99344 | 99492 | 99747 | 100012 | 100279 | 100540 | 100800 | 100947 | 101087 | 101252 | 101496 | 101745 | 102006 | 102250 | 102417 | 102560 | 102807 | 103052 | 103294 | 103547 | 103790 | 103949 | 104087 | 104335 | 104459
|  | DG | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3260 | 3260 | 3260 | 3260 | 3260 | 3260 | 3260 | 3260 | 3260 | 3260 | 3260 | 3260 | 3268 | 3276 | 3276 | 3276
6 | 3F | SL No 540430038646 (EB Unit) | 116441 | 116753 | 116974 | 117223 | 117482 | 117751 | 117891 | 118008 | 118301 | 118559 | 118851 | 119109 | 119393 | 119499 | 119617 | 119795 | 120070 | 120327 | 120599 | 120841 | 120969 | 121065 | 121334 | 121596 | 121855 | 122119 | 122379 | 122507 | 122647 | 122934 | 123060
|  | DG | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4244 | 4244 | 4244 | 4244 | 4244 | 4244 | 4244 | 4244 | 4244 | 4244 | 4244 | 4244 | 4250 | 4261 | 4261 | 4261
7 | 3F | SL No 540430038843 (EB Unit) | 378252 | 379282 | 380004 | 380733 | 381547 | 382327 | 382968 | 383491 | 384287 | 385096 | 385931 | 386708 | 387510 | 388116 | 388616 | 389153 | 389919 | 390697 | 391519 | 392266 | 392853 | 393313 | 394041 | 394825 | 395587 | 396409 | 397183 | 397787 | 398207 | 398990 | 399411
|  | DG | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11352 | 11352 | 11352 | 11352 | 11352 | 11352 | 11352 | 11352 | 11352 | 11352 | 11352 | 11352 | 11352 | 11600 | 11600 | 11600
8 | 3F | SL No 540430038848 (EB Unit) | 76796 | 76998 | 77124 | 77248 | 77371 | 77504 | 77607 | 77752 | 77884 | 78029 | 78157 | 78281 | 78281 | 78532 | 78689 | 78838 | 78958 | 79094 | 79215 | 79366 | 79482 | 79621 | 79758 | 79905 | 80035 | 80185 | 80325 | 80476 | 80565 | 80704 | 80798
|  | DG | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2201 | 2201 | 2201 | 2201 | 2201 | 2201 | 2201 | 2201 | 2201 | 2201 | 2201 | 2201 | 2207 | 2212 | 2212 | 2212
1 | 3F | AHU1 | 34660 | 34780 | 34932 | 35052 | 35251 | 35449 | 35641 | 35708 | 35876 | 35981 | 36056 | 36145 | 36250 | 36326 | 36361 | 36448 | 36585 | 36691 | 36762 | 36830 | 36556 | 36886 | 36963 | 37077 | 37184 | 37304 | 37426 | 37493 | 37516 | 37587 | 37637
|  | DG | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1918 | 1918 | 1918 | 1918 | 1918 | 1918 | 1918 | 1918 | 1918 | 1918 | 1918 | 1918 | 1918 | 1921 | 1921 | 1921
2 | 3F | AHU2 | 38471 | 38607 | 38752 | 38885 | 39076 | 39276 | 39464 | 39525 | 39708 | 39829 | 39960 | 40073 | 40191 | 40318 | 40361 | 40470 | 40608 | 40776 | 40869 | 40959 | 41025 | 41025 | 41123 | 41224 | 41361 | 41518 | 41653 | 41731 | 41758 | 41852 | 41922
|  | DG | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1909 | 1909 | 1909
3 | 3F | AHU3 | 41989 | 42143 | 42294 | 42445 | 42670 | 42901 | 43103 | 43252 | 43460 | 43589 | 43713 | 43840 | 43989 | 44089 | 44130 | 44217 | 44341 | 44471 | 44597 | 44713 | 44783 | 44783 | 44893 | 45062 | 45234 | 45404 | 45581 | 45735 | 45749 | 45914 | 45953
|  | DG | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2058 | 2058 | 2058 | 2058 | 2058 | 2058 | 2058 | 2058 | 2058 | 2058 | 2058 | 2058 | 2058 | 2065 | 2065 | 2065
4 | 3F | AHU4 | 33144 | 33289 | 33401 | 33525 | 33632 | 33738 | 33860 | 33861 | 33999 | 34081 | 34166 | 34261 | 34340 | 34394 | 34429 | 34496 | 34600 | 34698 | 34787 | 34875 | 34939 | 34939 | 35047 | 35149 | 35248 | 35353 | 35464 | 35553 | 35558 | 35666 | 35709
|  | DG | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1779 | 1779 | 1779 | 1779 | 1779 | 1779 | 1779 | 1779 | 1779 | 1779 | 1779 | 1779 | 1779 | 1786 | 1786 | 1786
1 | 3F | AHU1 - BTU | 345400 | 346008 | 346419 | 346968 | 347443 | 347969 | 348406 | 348406 | 349481 | 350187 | 350810 | 351468 | 351963 | 352293 | 352473 | 353087 | 353856 | 354556 | 355243 | 355948 | 356323 | 356329 | 356885 | 357547 | 358077 | 358615 | 359113 | 359666 | 359706 | 360376 | 360811
2 | 3F | AHU2 - BTU | 320953 | 321668 | 322316 | 322981 | 323518 | 324170 | 324646 | 324646 | 325954 | 326702 | 327439 | 328042 | 328658 | 329030 | 329234 | 330021 | 330724 | 331452 | 331947 | 332480 | 333015 | 333015 | 333752 | 334359 | 335057 | 335694 | 336323 | 336887 | 336936 | 337797 | 338439
3 | 3F | AHU3 - BTU | 335256 | 335875 | 336400 | 336888 | 337565 | 338154 | 339021 | 339021 | 340632 | 341333 | 341900 | 342533 | 343069 | 343312 | 343554 | 344468 | 345140 | 345871 | 346359 | 346940 | 347336 | 347336 | 348077 | 348849 | 349557 | 350075 | 350662 | 351326 | 351389 | 352341 | 353063
4 | 3F | AHU4 - BTU | 358992 | 359953 | 360704 | 361527 | 362427 | 363317 | 363937 | 363937 | 365234 | 366335 | 367191 | 368146 | 368993 | 369464 | 369699 | 370527 | 371468 | 372372 | 373227 | 374083 | 374557 | 374611 | 375463 | 376444 | 377302 | 378211 | 379061 | 379798 | 379916 | 380898 | 381662
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [31 empty] | Consumption
|  |  |  | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
|  | DG |  | Sun: 0; Tue: 0
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [32 empty] | EB
3 | 3F | AHU3 | [32 empty] | AHU
|  | DG | [32 empty] | BTU
4 | 3F | AHU4 | [32 empty] | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## Aug-25
AUG- 2025
Sr.No | Location | Meter | Previous Reading | 2025-08-01 | 2025-08-02 | 2025-08-03 | 2025-08-04 | 2025-08-05 | 2025-08-06 | 2025-08-07 | 2025-08-08 | 2025-08-09 | 2025-08-10 | 2025-08-11 | 2025-08-12 | 2025-08-13 | 2025-08-14 | 2025-08-15 | 2025-08-16 | 2025-08-17 | 2025-08-18 | 2025-08-19 | 2025-08-20 | 2025-08-21 | 2025-08-22 | 2025-08-23 | 2025-08-24 | 2025-08-25 | 2025-08-26 | 2025-08-27 | 2025-08-28 | 2025-08-29 | 2025-08-30 | 2025-08-31 | Consumption
|  |  |  | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun | Mon | Tue | Wed | Thu | Fri | Sat | Sun
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 129726 | 129984 | 130203 | 130405 | 130673 | 130960 | 131234 | 131571 | 131787 | 131986 | 132192 | 132461 | 132731 | 132992 | 133259 | 133471 | 133679 | 133890 | 134167 | 134443 | 134722 | 135007 | 135286 | 135502 | 135688 | 135986 | 136252 | 136541 | 136802 | 137069 | 137288 | 137403
|  | DG | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175 | 4175
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 189365 | 189738 | 190033 | 190307 | 190703 | 191130 | 191544 | 191958 | 192368 | 192635 | 192906 | 193302 | 193699 | 194108 | 194475 | 194759 | 195038 | 195321 | 195735 | 196151 | 196571 | 196996 | 197414 | 197702 | 197982 | 198390 | 198484 | 199212 | 199600 | 200003 | 200291 | 200443
|  | DG | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 91678 | 91896 | 92057 | 92185 | 92427 | 92681 | 92920 | 93161 | 93411 | 93531 | 93639 | 93873 | 94109 | 94358 | 94584 | 94704 | 94816 | 94927 | 95165 | 95406 | 95601 | 95915 | 96179 | 96317 | 96446 | 96701 | 96944 | 97198 | 97438 | 97696 | 97853 | 97925
|  | DG | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188
6 | 3F | SL No 540430038646 (EB Unit) | 110040 | 110257 | 110388 | 110486 | 110747 | 110991 | 111221 | 111514 | 111784 | 111850 | 111984 | 112228 | 112492 | 112764 | 112998 | 113092 | 113175 | 113290 | 113559 | 113829 | 114091 | 114361 | 114633 | 114762 | 114867 | 115152 | 115414 | 115707 | 115882 | 116245 | 116371 | 116441
|  | DG | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155
7 | 3F | SL No 540430038843 (EB Unit) | 357388 | 358179 | 358800 | 359312 | 360031 | 360852 | 361601 | 362383 | 363177 | 363653 | 364145 | 364885 | 365687 | 366465 | 367268 | 367558 | 367968 | 368435 | 369200 | 369977 | 370759 | 371538 | 372321 | 372938 | 373420 | 374161 | 374931 | 375767 | 376562 | 377376 | 378032 | 378252
|  | DG | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338
8 | 3F | SL No 540430038848 (EB Unit) | 72776 | 72915 | 73044 | 73171 | 73298 | 73437 | 73555 | 73702 | 73842 | 73969 | 74088 | 74260 | 74407 | 74533 | 74662 | 74777 | 74912 | 75039 | 75190 | 75318 | 75463 | 75585 | 75732 | 75846 | 75980 | 76117 | 76255 | 76380 | 76513 | 76628 | 76747 | 76796
|  | DG | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164
1 | 3F | AHU1 | 31560 | 31633 | 31706 | 31752 | 31839 | 31942 | 32043 | 32158 | 32300 | 32300 | 32315 | 32420 | 32573 | 32694 | 32835 | 32835 | 32931 | 32989 | 33129 | 33305 | 33471 | 33640 | 33793 | 33893 | 33893 | 34018 | 34107 | 34189 | 34336 | 34505 | 34660 | 34660
|  | DG | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882
2 | 3F | AHU2 | 35090 | 35275 | 35398 | 35418 | 35562 | 35734 | 35851 | 36046 | 36265 | 36265 | 36265 | 36411 | 36590 | 36727 | 36853 | 36853 | 36916 | 36971 | 37084 | 37214 | 37356 | 37487 | 37602 | 37664 | 37684 | 37796 | 37916 | 38020 | 38196 | 38357 | 38471 | 38471
|  | DG | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861
3 | 3F | AHU3 | 38186 | 38286 | 38442 | 38474 | 38606 | 38767 | 38921 | 39079 | 39224 | 39224 | 39224 | 39531 | 39693 | 39816 | 39948 | 39948 | 40005 | 40053 | 40180 | 40319 | 40427 | 40576 | 40720 | 40808 | 40808 | 40950 | 41061 | 41370 | 41596 | 41818 | 41989 | 41989
|  | DG | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016
4 | 3F | AHU4 | 30931 | 31022 | 31062 | 31078 | 31171 | 31264 | 31362 | 31456 | 31543 | 31543 | 31543 | 31652 | 31730 | 31793 | 31858 | 31858 | 31900 | 31934 | 32015 | 32100 | 32200 | 32302 | 32412 | 32416 | 32416 | 32529 | 32627 | 32733 | 32902 | 33035 | 33144 | 33144
|  | DG | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744
1 | 3F | AHU1 - BTU | 322263 | 323352 | 324270 | 324854 | 325967 | 327156 | 328550 | 329388 | 330305 | 330305 | 330521 | 331757 | 333267 | 334565 | 335539 | 335539 | 336061 | 336455 | 337768 | 339318 | 340373 | 340936 | 341615 | 342092 | 342111 | 342685 | 343238 | 343699 | 344329 | 344978 | 345400 | 345400
2 | 3F | AHU2 - BTU | 300479 | 301330 | 302186 | 302186 | 303550 | 304510 | 305363 | 306411 | 307453 | 307453 | 307564 | 308518 | 309429 | 310447 | 310964 | 310964 | 311492 | 311884 | 312965 | 314229 | 315102 | 315759 | 316517 | 316976 | 316990 | 317751 | 318386 | 318848 | 319648 | 320417 | 320953 | 320953
3 | 3F | AHU3 - BTU | 312610 | 313661 | 314469 | 314759 | 316092 | 317041 | 317956 | 318978 | 319705 | 319705 | 320110 | 321645 | 322818 | 323842 | 324452 | 324452 | 325078 | 325602 | 326648 | 327549 | 328463 | 329047 | 329749 | 330255 | 330264 | 331017 | 331861 | 332763 | 333608 | 334603 | 335256 | 335256
4 | 3F | AHU4 - BTU | 337491 | 338457 | 339026 | 339026 | 340091 | 341102 | 342103 | 343092 | 344103 | 344103 | 344400 | 345485 | 346471 | 347315 | 347995 | 347995 | 348332 | 348523 | 349471 | 350523 | 351547 | 352461 | 353303 | 353486 | 353544 | 354459 | 355467 | 356180 | 357263 | 358394 | 358992 | 358992
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | FRI
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
|  | DG |  | MON: 0; WED: 0
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [33 empty] | EB
3 | 3F | AHU3 | [33 empty] | AHU
|  | DG | [33 empty] | BTU
4 | 3F | AHU4 | [33 empty] | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## July-2025
JULY- 2025
Sr.No | Location | Meter | Previous Reading | 2025-07-01 | 2025-07-02 | 2025-07-03 | 2025-07-04 | 2025-07-05 | 2025-07-06 | 2025-07-07 | 2025-07-08 | 2025-07-09 | 2025-07-10 | 2025-07-11 | 2025-07-12 | 2025-07-13 | 2025-07-14 | 2025-07-15 | 2025-07-16 | 2025-07-17 | 2025-07-18 | 2025-07-19 | 2025-07-20 | 2025-07-21 | 2025-07-22 | 2025-07-23 | 2025-07-24 | 2025-07-25 | 2025-07-26 | 2025-07-27 | 2025-07-28 | 2025-07-29 | 2025-07-30 | 2025-07-31 | Consumption
|  |  |  | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | FRI
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 121887 | 122258 | 122537 | 122822 | 123086 | 123298 | 123509 | 123768 | 124053 | 124348 | 124588 | 124844 | 125058 | 125266 | 125537 | 125798 | 126085 | 126357 | 126630 | 126845 | 127055 | 127329 | 127600 | 127877 | 128171 | 128449 | 128540 | 128631 | 128896 | 129149 | 129459 | 129726
|  | DG | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 177601 | 178152 | 178565 | 178987 | 179383 | 179664 | 179955 | 180329 | 180751 | 181190 | 181542 | 181922 | 182209 | 182488 | 182883 | 183279 | 183698 | 184108 | 184511 | 184716 | 185078 | 185477 | 185887 | 186297 | 186737 | 187156 | 187456 | 187732 | 188128 | 188535 | 188971 | 189365
|  | DG | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 85219 | 85521 | 85757 | 85997 | 86223 | 86359 | 86473 | 86688 | 86931 | 87176 | 87381 | 87601 | 87736 | 87857 | 88062 | 88294 | 88535 | 88777 | 89018 | 89153 | 89271 | 89490 | 89724 | 89963 | 90226 | 90469 | 90570 | 90703 | 90937 | 91182 | 91443 | 91678
|  | DG | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188
6 | 3F | SL No 540430038646 (EB Unit) | 103012 | 103406 | 103649 | 103933 | 104186 | 104295 | 104391 | 104639 | 104891 | 105179 | 105401 | 105644 | 105746 | 105849 | 106079 | 106332 | 106573 | 106827 | 107048 | 107174 | 107262 | 107525 | 107762 | 108037 | 108316 | 108572 | 108805 | 108970 | 109230 | 109509 | 109772 | 110040
|  | DG | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155
7 | 3F | SL No 540430038843 (EB Unit) | 335272 | 336369 | 337172 | 337996 | 338746 | 339321 | 339688 | 340463 | 341238 | 342025 | 342710 | 343416 | 343960 | 344403 | 345142 | 345894 | 346691 | 347485 | 348250 | 348781 | 349208 | 349928 | 350704 | 351483 | 352300 | 353078 | 353837 | 354305 | 355025 | 355806 | 356626 | 357388
|  | DG | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11388 | 11388 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338
8 | 3F | SL No 540430038848 (EB Unit) | 68756 | 68923 | 69072 | 69206 | 69330 | 69445 | 69590 | 69726 | 69880 | 70027 | 70153 | 70271 | 70401 | 70520 | 70666 | 70787 | 70933 | 71061 | 71202 | 71311 | 71443 | 71570 | 71706 | 71826 | 71906 | 72107 | 72175 | 72250 | 72404 | 72523 | 72662 | 72776
|  | DG | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164
1 | 3F | AHU1 | 29197 | 29293 | 29351 | 29438 | 29516 | 29550 | 29550 | 29618 | 29674 | 29731 | 29797 | 29844 | 29871 | 29871 | 29954 | 30073 | 30180 | 30336 | 30460 | 30525 | 30525 | 30606 | 30686 | 30814 | 30923 | 31059 | 31110 | 31110 | 31247 | 31381 | 31479 | 31560
|  | DG | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882
2 | 3F | AHU2 | 31895 | 32095 | 32233 | 32371 | 32493 | 32564 | 32564 | 32696 | 32803 | 32922 | 33026 | 33148 | 33216 | 33216 | 33330 | 33467 | 33548 | 33663 | 33779 | 33843 | 33843 | 33953 | 34063 | 34185 | 34334 | 34442 | 34550 | 34550 | 34676 | 34808 | 34992 | 35090
|  | DG | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861
3 | 3F | AHU3 | 34710 | 34905 | 35056 | 35193 | 35343 | 35418 | 35418 | 35528 | 35637 | 35734 | 35819 | 35911 | 35967 | 35967 | 36073 | 36207 | 36321 | 36462 | 36657 | 36724 | 36724 | 36883 | 37063 | 37197 | 37339 | 37496 | 37585 | 37585 | 37751 | 37921 | 38086 | 38186
|  | DG | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016
4 | 3F | AHU4 | 28719 | 28867 | 28968 | 29063 | 29166 | 29226 | 29226 | 29315 | 29401 | 29485 | 29561 | 29635 | 29635 | 29684 | 29779 | 29858 | 29922 | 30001 | 30063 | 30091 | 30091 | 30157 | 30220 | 30287 | 30380 | 30484 | 30549 | 30549 | 30658 | 30760 | 30853 | 30931
|  | DG | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744
1 | 3F | AHU1 - BTU | 291798 | 293068 | 294337 | 295601 | 296557 | 297287 | 297287 | 298846 | 300013 | 301206 | 302104 | 302935 | 303270 | 303270 | 304551 | 305964 | 306846 | 307968 | 308971 | 310288 | 310288 | 311594 | 313252 | 314047 | 315016 | 316403 | 317257 | 317257 | 318952 | 320167 | 321228 | 322263
2 | 3F | AHU2 - BTU | 279049 | 279832 | 280712 | 281416 | 282094 | 282428 | 282428 | 283309 | 284319 | 285116 | 285827 | 286593 | 287210 | 287210 | 288184 | 289016 | 289760 | 290548 | 291341 | 291713 | 291713 | 292668 | 293359 | 294020 | 295088 | 296041 | 296847 | 296847 | 297987 | 298190 | 299330 | 300479
3 | 3F | AHU3 - BTU | 283579 | 284646 | 285803 | 286915 | 287648 | 288613 | 288613 | 289741 | 290969 | 291951 | 292772 | 293809 | 294418 | 294418 | 295504 | 296909 | 297939 | 299298 | 300298 | 301108 | 301108 | 301434 | 303587 | 304685 | 305839 | 307156 | 308119 | 308119 | 309370 | 310380 | 311549 | 312610
4 | 3F | AHU4 - BTU | 309779 | 310939 | 311987 | 313180 | 314310 | 314935 | 314935 | 316129 | 317166 | 318136 | 319101 | 319980 | 320534 | 320534 | 321773 | 323058 | 324106 | 325311 | 326379 | 326895 | 326995 | 328090 | 329090 | 330169 | 331247 | 332505 | 333257 | 333257 | 334613 | 335642 | 336645 | 337491
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | FRI
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit) |  | SUN: 0; MON: 0; SAT: 0; SUN: 0
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
|  | DG |  | MON: 0; WED: 0
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [33 empty] | EB
3 | 3F | AHU3 | [33 empty] | AHU
|  | DG | [33 empty] | BTU
4 | 3F | AHU4 |  | MON: 66 |  | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU |  | MON: 1306
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU |  | MON: 1326
4 | 3F | AHU4 - BTU
Total BTU Consumption

## June - 2025
JUNE - 2025
Sr.No | Location | Meter | Previous Reading | 2025-06-01 | 2025-06-02 | 2025-06-03 | 2025-06-04 | 2025-06-05 | 2025-06-06 | 2025-06-07 | 2025-06-08 | 2025-06-09 | 2025-06-10 | 2025-06-11 | 2025-06-12 | 2025-06-13 | 2025-06-14 | 2025-06-15 | 2025-06-16 | 2025-06-17 | 2025-06-18 | 2025-06-19 | 2025-06-20 | 2025-06-21 | 2025-06-22 | 2025-06-23 | 2025-06-24 | 2025-06-25 | 2025-06-26 | 2025-06-27 | 2025-06-28 | 2025-06-29 | 2025-06-30 | 2025-05-31 | Consumption
|  |  |  | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | SAT
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 114025 | 114691 | 114949 | 115216 | 115489 | 115763 | 116035 | 116247 | 116455 | 116705 | 116965 | 117229 | 117492 | 117762 | 117979 | 118172 | 118437 | 118709 | 118983 | 119260 | 119523 | 119726 | 119933 | 120201 | 120476 | 120772 | 121034 | 121298 | 121510 | 121718 | 121887
|  | DG | 4136 | 4144 | 4144 | 4144 | 4144 | 4144 | 4144 | 4144 | 4144 | 4144 | 4144 | 4161 | 4161 | 4161 | 4161 | 4161 | 4161 | 4161 | 4161 | 4161 | 4161 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176 | 4176
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 166335 | 167247 | 167618 | 168009 | 168413 | 168816 | 169220 | 169500 | 169774 | 170128 | 170507 | 170897 | 171285 | 171686 | 171975 | 172230 | 172618 | 173020 | 173424 | 173835 | 174219 | 174471 | 174774 | 175170 | 175573 | 176012 | 176401 | 176781 | 177079 | 177353 | 177601
|  | DG | 6189 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6200 | 6222 | 6222 | 6222 | 6222 | 6222 | 6222 | 6222 | 6222 | 6222 | 6222 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242 | 6242
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 79294 | 79761 | 79971 | 80178 | 80393 | 80620 | 80839 | 80972 | 81089 | 81283 | 81486 | 81686 | 81893 | 82107 | 82247 | 82370 | 82586 | 82807 | 83020 | 83244 | 83458 | 83594 | 83719 | 83927 | 84147 | 84381 | 84596 | 84813 | 84961 | 85093 | 85219
|  | DG | 3162 | 3167 | 3167 | 3167 | 3167 | 3167 | 3167 | 3167 | 3167 | 3167 | 3167 | 3177 | 3177 | 3177 | 3177 | 3177 | 3177 | 3177 | 3177 | 3177 | 3177 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188 | 3188
6 | 3F | SL No 540430038646 (EB Unit) | 96236 | 96688 | 96950 | 97214 | 97501 | 97762 | 98052 | 98157 | 98264 | 98526 | 98789 | 99059 | 99336 | 99608 | 99727 | 99838 | 100107 | 100364 | 100626 | 100882 | 101127 | 101193 | 101285 | 101525 | 101812 | 102102 | 102365 | 102652 | 102769 | 102883 | 103012
|  | DG | 4135 | 4137 | 4137 | 4137 | 4137 | 4137 | 4137 | 4137 | 4137 | 4137 | 4137 | 4150 | 4150 | 4150 | 4150 | 4150 | 4150 | 4150 | 4150 | 4150 | 4150 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155 | 4155
7 | 3F | SL No 540430038843 (EB Unit) | 315463 | 317116 | 317835 | 318539 | 319247 | 319967 | 320711 | 321252 | 321573 | 322261 | 322986 | 323665 | 324382 | 325097 | 325689 | 326045 | 326750 | 327478 | 328207 | 328939 | 329627 | 330079 | 330374 | 331032 | 331749 | 332542 | 333211 | 333909 | 334503 | 334891 | 335272
|  | DG | 11237 | 11252 | 11252 | 11252 | 11252 | 11252 | 11252 | 11252 | 11252 | 11252 | 11252 | 11286 | 11286 | 11286 | 11286 | 11286 | 11286 | 11286 | 11286 | 11286 | 11286 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338 | 11338
8 | 3F | SL No 540430038848 (EB Unit) | 64289 | 64667 | 64800 | 64945 | 65023 | 65207 | 65338 | 65470 | 65619 | 65798 | 65947 | 66114 | 66258 | 66413 | 66548 | 66685 | 66819 | 66968 | 67100 | 67250 | 67379 | 67539 | 67686 | 67825 | 67972 | 68114 | 68257 | 68385 | 68534 | 68648 | 68756
|  | DG | 2136 | 2143 | 2143 | 2143 | 2143 | 2143 | 2143 | 2143 | 2143 | 2143 | 2143 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2152 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164 | 2164
1 | 3F | AHU1 | 27563 | 27658 | 27729 | 27797 | 27862 | 27928 | 27998 | 28037 | 28037 | 28118 | 28191 | 28266 | 28326 | 28372 | 28403 | 28403 | 28481 | 28550 | 28625 | 28697 | 28761 | 28809 | 28809 | 28886 | 28958 | 29014 | 29064 | 29115 | 29164 | 29164 | 29197
|  | DG | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1898 | 1898 | 1898 | 1898 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882 | 1882
2 | 3F | AHU2 | 29426 | 29570 | 29659 | 29751 | 29849 | 29948 | 30049 | 30108 | 30108 | 30218 | 30331 | 30442 | 30552 | 30639 | 30706 | 30706 | 30805 | 30898 | 31009 | 31095 | 31192 | 31264 | 31264 | 31379 | 31450 | 31535 | 31644 | 31753 | 31843 | 31843 | 31895
|  | DG | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861 | 1861
3 | 3F | AHU3 | 31727 | 31924 | 32035 | 32155 | 32276 | 32408 | 32539 | 32611 | 32611 | 32744 | 32873 | 33006 | 33129 | 33223 | 33284 | 33284 | 33406 | 33530 | 33656 | 33782 | 33904 | 33986 | 33986 | 34112 | 34239 | 34352 | 34460 | 34564 | 34657 | 34657 | 34710
|  | DG | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016 | 2016
4 | 3F | AHU4 | 26464 | 26586 | 26681 | 26774 | 26862 | 26952 | 27044 | 27096 | 27096 | 27192 | 27289 | 27387 | 27472 | 27547 | 27600 | 27600 | 27697 | 27789 | 27884 | 27979 | 28063 | 28124 | 28124 | 28224 | 28320 | 28413 | 28509 | 28600 | 28675 | 28675 | 28719
|  | DG | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744 | 1744
3
1 | 3F | AHU1 - BTU | 264315 | 265888 | 266949 | 267962 | 268907 | 269942 | 271005 | 271446 | 271446 | 272720 | 273688 | 274698 | 275797 | 276967 | 277513 | 277513 | 278842 | 280005 | 281190 | 282262 | 283424 | 284039 | 284039 | 285368 | 286501 | 287485 | 288794 | 289890 | 290505 | 290505 | 291798
2 | 3F | AHU2 - BTU | 258287 | 259417 | 260330 | 261118 | 261778 | 262480 | 263161 | 263656 | 263656 | 264709 | 265519 | 266392 | 267187 | 267995 | 268659 | 268659 | 269674 | 270429 | 271196 | 271981 | 272740 | 273341 | 273341 | 274502 | 275325 | 276001 | 276916 | 277649 | 278165 | 278165 | 279049
3 | 3F | AHU3 - BTU | 257817 | 259278 | 260329 | 261080 | 261724 | 262225 | 262820 | 263479 | 263479 | 264867 | 266018 | 267214 | 268249 | 269452 | 270184 | 270184 | 271459 | 272506 | 273564 | 274665 | 275894 | 276499 | 276499 | 277965 | 278939 | 279806 | 280835 | 281728 | 282412 | 282412 | 283579
4 | 3F | AHU4 - BTU | 283828 | 285318 | 286382 | 287399 | 288330 | 289337 | 290329 | 290752 | 290752 | 291958 | 292886 | 293829 | 294815 | 295840 | 296339 | 296339 | 297530 | 298699 | 299729 | 300655 | 301647 | 302224 | 302224 | 303598 | 304688 | 305598 | 306878 | 307930 | 308516 | 308516 | 309779
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit) |  | FRI: 0; SAT: 0; THU: 0; FRI: 0
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
|  | DG | [33 empty] | EB
3 | 3F | AHU3 | [33 empty] | AHU
|  | DG | [33 empty] | BTU
4 | 3F | AHU4 | [33 empty] | DG
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## May-2025
MAY-2025
Sr.No | Location | Meter | Previous Reading | 2025-05-01 | 2025-05-02 | 2025-05-03 | 2025-05-04 | 2025-05-05 | 2025-05-06 | 2025-05-07 | 2025-05-08 | 2025-05-09 | 2025-05-10 | 2025-05-11 | 2025-05-12 | 2025-05-13 | 2025-05-14 | 2025-05-15 | 2025-05-16 | 2025-05-17 | 2025-05-18 | 2025-05-19 | 2025-05-20 | 2025-05-21 | 2025-05-22 | 2025-05-23 | 2025-05-24 | 2025-05-25 | 2025-05-26 | 2025-05-27 | 2025-05-28 | 2025-05-29 | 2025-05-30 | 2025-05-31 | Consumption
|  |  |  | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 106913 | 107184 | 107435 | 107629 | 107819 | 108087 | 108344 | 108596 | 108856 | 109113 | 109305 | 109509 | 109765 | 110014 | 110298 | 110568 | 110819 | 111021 | 111225 | 111494 | 111762 | 112036 | 112311 | 112565 | 112770 | 112968 | 113223 | 113491 | 113759 | 114025 | 114282 | 114498
|  | DG | 4118 | 4118 | 4118 | 4118 | 4118 | 4118 | 4118 | 4118 | 4118 | 4118 | 4118 | 4118 | 4118 | 4118 | 4118 | 4122 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4131 | 4136 | 4136 | 4136 | 4136 | 4136 | 4144
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 156211 | 156582 | 156939 | 157193 | 157439 | 157828 | 158204 | 158569 | 158953 | 159320 | 159576 | 159837 | 160220 | 160616 | 161007 | 161401 | 161767 | 162033 | 162276 | 162697 | 163092 | 163497 | 163899 | 164272 | 164539 | 164795 | 165259 | 165550 | 165901 | 166335 | 166711 | 166996
|  | DG | 6164 | 6164 | 6164 | 6164 | 6164 | 6164 | 6164 | 6164 | 6164 | 6164 | 6164 | 6164 | 6164 | 6164 | 6164 | 6169 | 6183 | 6183 | 6183 | 6183 | 6183 | 6183 | 6183 | 6183 | 6183 | 6183 | 6189 | 6189 | 6189 | 6189 | 6189 | 6200
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 73751 | 73958 | 74156 | 74293 | 74422 | 74649 | 74874 | 75087 | 75307 | 75513 | 75636 | 75747 | 75956 | 76174 | 76395 | 76622 | 76830 | 76943 | 77053 | 77272 | 77492 | 77726 | 77967 | 78185 | 78324 | 78429 | 78638 | 78848 | 79078 | 79294 | 79503 | 79648
|  | DG | 3149 | 3149 | 3149 | 3149 | 3149 | 3149 | 3149 | 3149 | 3149 | 3149 | 3149 | 3149 | 3149 | 3149 | 3149 | 3151 | 3159 | 3159 | 3159 | 3159 | 3159 | 3159 | 3159 | 3159 | 3159 | 3159 | 3162 | 3162 | 3162 | 3162 | 3162 | 3167
6 | 3F | SL No 540430038646 (EB Unit) | 89738 | 89990 | 90245 | 90358 | 90496 | 90738 | 91014 | 91264 | 91549 | 91805 | 91933 | 92045 | 92312 | 92561 | 92826 | 93104 | 93366 | 93473 | 93641 | 93915 | 94200 | 94479 | 94739 | 94989 | 95089 | 95205 | 95435 | 95705 | 95965 | 96236 | 96478 | 96593
|  | DG | 4115 | 4115 | 4115 | 4115 | 4115 | 4115 | 4115 | 4115 | 4115 | 4115 | 4115 | 4115 | 4115 | 4115 | 4115 | 4117 | 4128 | 4128 | 4128 | 4128 | 4128 | 4128 | 4128 | 4128 | 4128 | 4128 | 4135 | 4135 | 4135 | 4135 | 4135 | 4137
7 | 3F | SL No 540430038843 (EB Unit) | 295586 | 296344 | 297135 | 297721 | 298186 | 298967 | 299719 | 300451 | 301215 | 301956 | 302453 | 302782 | 303520 | 304301 | 305075 | 305824 | 306569 | 307168 | 307652 | 308419 | 309183 | 309964 | 310749 | 311500 | 312083 | 312515 | 313259 | 313995 | 314756 | 315463 | 316184 | 316770
|  | DG | 11189 | 11189 | 11189 | 11189 | 11189 | 11189 | 11189 | 11189 | 11189 | 11189 | 11189 | 11189 | 11189 | 11189 | 11189 | 11198 | 11222 | 11222 | 11222 | 11222 | 11222 | 11222 | 11222 | 11222 | 11222 | 11222 | 11237 | 11237 | 11237 | 11237 | 11237 | 11252
8 | 3F | SL No 540430038848 (EB Unit) | 59619 | 59808 | 59963 | 60126 | 60257 | 60449 | 60601 | 60756 | 60935 | 61120 | 61245 | 61431 | 61597 | 61802 | 61963 | 62175 | 62338 | 62513 | 62624 | 62800 | 63002 | 63166 | 63344 | 63461 | 63619 | 63728 | 63876 | 64009 | 64161 | 64289 | 64434 | 64545
|  | DG | 2128 | 2128 | 2128 | 2128 | 2128 | 2128 | 2128 | 2128 | 2128 | 2128 | 2128 | 2128 | 2128 | 2128 | 2128 | 2130 | 2134 | 2134 | 2134 | 2134 | 2134 | 2134 | 2134 | 2134 | 2134 | 2134 | 2136 | 2136 | 2136 | 2136 | 2136 | 2143
1 | 3F | AHU1 | 26337 | 26397 | 26460 | 26499 | 26499 | 26534 | 26565 | 26604 | 26646 | 26688 | 26714 | 26714 | 26763 | 26809 | 26845 | 26905 | 26947 | 26972 | 26973 | 27054 | 27110 | 27171 | 27219 | 27268 | 27292 | 27292 | 27367 | 27439 | 27506 | 27563 | 27621 | 27658
|  | DG | 1876 | 1876 | 1876 | 1876 | 1876 | 1876 | 1876 | 1876 | 1876 | 1876 | 1876 | 1876 | 1876 | 1876 | 1876 | 1876 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878 | 1878
2 | 3F | AHU2 | 27621 | 27703 | 27771 | 27804 | 27804 | 27870 | 27929 | 27975 | 28050 | 28130 | 28173 | 28173 | 28262 | 28345 | 28434 | 28522 | 28582 | 28624 | 28625 | 28730 | 28840 | 28938 | 29015 | 29083 | 29118 | 29118 | 29204 | 29288 | 29350 | 29426 | 29507 | 29570
|  | DG | 1855 | 1855 | 1855 | 1855 | 1855 | 1855 | 1855 | 1855 | 1855 | 1855 | 1855 | 1855 | 1855 | 1855 | 1855 | 1855 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857 | 1857
3 | 3F | AHU3 | 29154 | 29273 | 29392 | 29463 | 29463 | 29572 | 29682 | 29784 | 29896 | 29990 | 30032 | 30032 | 30140 | 30251 | 30361 | 30476 | 30562 | 30623 | 30624 | 30725 | 30853 | 30979 | 31082 | 31206 | 31276 | 31276 | 31378 | 31498 | 31623 | 31727 | 31839 | 31924
|  | DG | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005 | 2005
4 | 3F | AHU4 | 24643 | 24732 | 24821 | 24876 | 24876 | 24963 | 25045 | 25098 | 25154 | 25210 | 25244 | 25244 | 25304 | 25361 | 25421 | 25479 | 25527 | 25559 | 25559 | 25656 | 25764 | 25872 | 25964 | 26057 | 26103 | 26103 | 26203 | 26300 | 26387 | 26464 | 26538 | 26586
|  | DG | 1736 | 1736 | 1736 | 1736 | 1736 | 1736 | 1736 | 1736 | 1736 | 1736 | 1736 | 1736 | 1736 | 1736 | 1736 | 1736 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739 | 1739
1 | 3F | AHU1 - BTU | 241097 | 242086 | 242985 | 243555 | 243555 | 244595 | 245525 | 246403 | 247294 | 248175 | 248557 | 248557 | 249668 | 250522 | 251517 | 252344 | 253139 | 253582 | 253582 | 255018 | 256248 | 257442 | 258366 | 259334 | 259807 | 259807 | 261113 | 262236 | 263263 | 264315 | 265337 | 265888
2 | 3F | AHU2 - BTU | 241385 | 242077 | 242589 | 242852 | 242852 | 243585 | 244270 | 244823 | 245387 | 246070 | 246331 | 246331 | 247228 | 248015 | 248825 | 249556 | 250191 | 250510 | 250510 | 251699 | 252623 | 253466 | 254176 | 254907 | 255145 | 255145 | 256027 | 256784 | 257528 | 258287 | 258858 | 259417
3 | 3F | AHU3 - BTU | 237325 | 238030 | 238530 | 238808 | 238808 | 239749 | 240412 | 240947 | 241812 | 242618 | 242850 | 242850 | 243888 | 244869 | 245894 | 246699 | 247536 | 247750 | 247750 | 248978 | 250362 | 251556 | 252373 | 253287 | 253441 | 253441 | 254687 | 255521 | 256583 | 257817 | 258532 | 259278
4 | 3F | AHU4 - BTU | 262507 | 263374 | 264092 | 264569 | 264569 | 265515 | 266380 | 267137 | 267987 | 268825 | 269222 | 269222 | 270200 | 270966 | 271869 | 272650 | 273363 | 273765 | 273765 | 275069 | 276208 | 277343 | 278268 | 279211 | 279609 | 279609 | 280781 | 281801 | 282806 | 283828 | 284763 | 285318
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 9:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit) |  | 2025-05-12: 0; 2025-05-13: 0
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3 | [33 empty] | EB
|  | DG | [33 empty] | AHU
4 | 3F | AHU4 | [33 empty] | BTU
|  | DG | [33 empty] | DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## April-2025
APRIL-25
Sr.No | Location | Meter | Previous Reading | 2025-04-01 | 2025-04-02 | 2025-04-03 | 2025-04-04 | 2025-04-05 | 2025-04-06 | 2025-04-07 | 2025-04-08 | 2025-04-09 | 2025-04-10 | 2025-04-11 | 2025-04-12 | 2025-04-13 | 2025-04-14 | 2025-04-15 | 2025-04-16 | 2025-04-17 | 2025-04-18 | 2025-04-19 | 2025-04-20 | 2025-04-21 | 2025-04-22 | 2025-04-23 | 2025-04-24 | 2025-04-25 | 2025-04-26 | 2025-04-27 | 2025-04-28 | 2025-04-29 | 2025-04-30 | Consumption
|  |  |  | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 99316 | 99689 | 99966 | 100236 | 100510 | 100722 | 100937 | 101202 | 101476 | 101749 | 102027 | 102299 | 102506 | 102709 | 102975 | 103249 | 103510 | 103733 | 103977 | 104182 | 104379 | 104624 | 104883 | 105149 | 105315 | 105574 | 105773 | 105972 | 106231 | 106505 | 106913
|  | DG | 3970 | 3970 | 3970 | 3970 | 3970 | 3970 | 3970 | 3970 | 3970 | 3970 | 3970 | 3970 | 3970 | 3970 | 3970 | 3970 | 3970 | 4012 | 4012 | 4012 | 4012 | 4012 | 4012 | 4012 | 4113 | 4118 | 4118 | 4118 | 4118 | 4118 | 4118
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 145395 | 145930 | 146340 | 146716 | 147148 | 147438 | 147726 | 148112 | 148516 | 148923 | 149411 | 149823 | 150102 | 150370 | 150765 | 151167 | 151555 | 151880 | 152224 | 152448 | 152755 | 153103 | 153477 | 153872 | 154110 | 154483 | 154748 | 155011 | 155393 | 155794 | 156211
|  | DG | 5938 | 5938 | 5938 | 5938 | 5938 | 5938 | 5938 | 5938 | 5938 | 5938 | 5938 | 5938 | 5938 | 5938 | 5938 | 5938 | 5938 | 6002 | 6002 | 6002 | 6002 | 6002 | 6002 | 6002 | 6157 | 6164 | 6164 | 6164 | 6164 | 6164 | 6164
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 68389 | 68656 | 68868 | 69063 | 69256 | 69339 | 69428 | 69626 | 69848 | 70069 | 70290 | 70501 | 70611 | 70723 | 70929 | 71147 | 71362 | 71536 | 71719 | 71833 | 71951 | 72153 | 72359 | 72583 | 72713 | 72912 | 73013 | 73102 | 73309 | 73521 | 73751
|  | DG | 3018 | 3018 | 3018 | 3018 | 3018 | 3018 | 3018 | 3018 | 3018 | 3018 | 3018 | 3018 | 3018 | 3018 | 3018 | 3018 | 3018 | 3054 | 3054 | 3054 | 3054 | 3054 | 3054 | 3054 | 3145 | 3149 | 3149 | 3149 | 3149 | 3149 | 3149
6 | 3F | SL No 540430038646 (EB Unit) | 82927 | 83233 | 83508 | 83782 | 84070 | 84170 | 84306 | 84574 | 84869 | 85133 | 85433 | 85714 | 85839 | 85938 | 86224 | 86480 | 86776 | 86992 | 87256 | 87379 | 87492 | 87766 | 88049 | 88327 | 88490 | 88752 | 88854 | 88954 | 89219 | 89471 | 89738
|  | DG | 3935 | 3935 | 3935 | 3935 | 3935 | 3935 | 3935 | 3935 | 3935 | 3935 | 3935 | 3935 | 3935 | 3935 | 3935 | 3935 | 3935 | 3984 | 3984 | 3984 | 3984 | 3984 | 3984 | 3984 | 4111 | 4115 | 4115 | 4115 | 4115 | 4115 | 4115
7 | 3F | SL No 540430038843 (EB Unit) | 275737 | 276527 | 277268 | 277968 | 278677 | 279138 | 279576 | 280282 | 280995 | 281742 | 282497 | 283238 | 283826 | 284315 | 285041 | 285798 | 286511 | 287147 | 287882 | 288470 | 288976 | 289662 | 290311 | 291081 | 291523 | 292273 | 292832 | 293259 | 294017 | 294785 | 295586
|  | DG | 10746 | 10746 | 10746 | 10746 | 10746 | 10746 | 10746 | 10746 | 10746 | 10746 | 10746 | 10746 | 10746 | 10746 | 10746 | 10746 | 10746 | 10874 | 10874 | 10874 | 10874 | 10874 | 10874 | 10874 | 11171 | 11189 | 11189 | 11189 | 11189 | 11189 | 11189
8 | 3F | SL No 540430038848 (EB Unit) | 55458 | 55635 | 55753 | 55881 | 55997 | 56103 | 56222 | 56397 | 56538 | 56724 | 56869 | 57020 | 57135 | 57284 | 57421 | 57593 | 57724 | 57885 | 58022 | 58180 | 58301 | 58480 | 58507 | 58729 | 58786 | 58915 | 59026 | 59159 | 59293 | 59455 | 59619
|  | DG | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2066 | 2066 | 2066 | 2066 | 2066 | 2066 | 2066 | 2126 | 2128 | 2128 | 2128 | 2128 | 2128 | 2128
1 | 3F | AHU1 | 25188 | 25249 | 25291 | 25335 | 25376 | 25406 | 25406 | 25490 | 25540 | 25580 | 25630 | 25675 | 25697 | 25697 | 25767 | 25816 | 25853 | 25878 | 25914 | 25933 | 25933 | 26010 | 26047 | 26081 | 26109 | 26142 | 26160 | 26160 | 26209 | 26273 | 26337
|  | DG | 1832 | 1832 | 1832 | 1832 | 1832 | 1832 | 1832 | 1832 | 1832 | 1832 | 1832 | 1832 | 1832 | 1832 | 1832 | 1832 | 1832 | 1842 | 1842 | 1842 | 1842 | 1842 | 1842 | 1842 | 1876 | 1876 | 1876 | 1876 | 1876 | 1876 | 1876
2 | 3F | AHU2 | 25865 | 25918 | 25966 | 26014 | 26060 | 26093 | 26093 | 26178 | 26247 | 26295 | 26340 | 26445 | 26496 | 26496 | 26583 | 26733 | 26851 | 26908 | 26974 | 27011 | 27011 | 27104 | 27173 | 27244 | 27272 | 27324 | 27350 | 27350 | 27420 | 27524 | 27621
|  | DG | 1797 | 1797 | 1797 | 1797 | 1797 | 1797 | 1797 | 1797 | 1797 | 1797 | 1797 | 1797 | 1797 | 1797 | 1797 | 1797 | 1797 | 1816 | 1816 | 1816 | 1816 | 1816 | 1816 | 1816 | 1853 | 1855 | 1855 | 1855 | 1855 | 1855 | 1855
3 | 3F | AHU3 | 27082 | 27156 | 27205 | 27254 | 27299 | 27337 | 27338 | 27435 | 27514 | 27560 | 27599 | 27711 | 27760 | 27760 | 27823 | 27964 | 28095 | 28180 | 28296 | 28357 | 28357 | 28465 | 28520 | 28635 | 28688 | 28763 | 28791 | 28791 | 28904 | 29027 | 29154
|  | DG | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1938 | 1938 | 1938 | 1938 | 1938 | 1938 | 1938 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002 | 2002
4 | 3F | AHU4 | 23227 | 23276 | 23329 | 23385 | 23434 | 23473 | 23473 | 23545 | 23598 | 23647 | 23700 | 23749 | 23801 | 23801 | 23862 | 23920 | 23976 | 24009 | 24072 | 24099 | 24099 | 24188 | 24235 | 24284 | 24313 | 24358 | 24392 | 24392 | 24451 | 24550 | 24643
|  | DG | 1686 | 1686 | 1686 | 1686 | 1686 | 1686 | 1686 | 1686 | 1686 | 1686 | 1686 | 1686 | 1686 | 1686 | 1686 | 1686 | 1686 | 1700 | 1700 | 1700 | 1700 | 1700 | 1700 | 1700 | 1736 | 1736 | 1736 | 1736 | 1736 | 1736 | 1736
1 | 3F | AHU1 - BTU | 220563 | 221384 | 222088 | 222781 | 223443 | 223703 | 223703 | 224701 | 225577 | 226449 | 227369 | 228116 | 228440 | 228440 | 229544 | 230532 | 231469 | 232358 | 233156 | 233534 | 233534 | 234608 | 235453 | 236264 | 237119 | 237853 | 238104 | 238104 | 239049 | 240029 | 241097
2 | 3F | AHU2 - BTU | 224872 | 225476 | 226061 | 226649 | 227224 | 227434 | 227439 | 228254 | 228974 | 229643 | 230424 | 231110 | 231282 | 231282 | 232115 | 232788 | 233480 | 234148 | 234703 | 234995 | 234995 | 235872 | 236651 | 237330 | 237937 | 238498 | 238799 | 238799 | 239743 | 240585 | 241385
3 | 3F | AHU3 - BTU | 220395 | 221076 | 221682 | 222319 | 222994 | 223139 | 223139 | 223840 | 224485 | 225212 | 226072 | 226925 | 227336 | 227336 | 228185 | 228973 | 229563 | 230155 | 230835 | 231011 | 231011 | 231966 | 232644 | 233345 | 233934 | 234482 | 234775 | 234775 | 235729 | 236512 | 237325
4 | 3F | AHU4 - BTU | 244029 | 244714 | 245366 | 246018 | 246641 | 246885 | 246885 | 247758 | 248517 | 249284 | 250075 | 250830 | 251131 | 251131 | 251983 | 252798 | 253588 | 254370 | 255064 | 255390 | 255390 | 256333 | 257134 | 257893 | 258731 | 259408 | 259663 | 259663 | 260528 | 261522 | 262507
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [31 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit) |  | 2025-04-12: 0; 2025-04-13: 0
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit) | [32 empty] | EB
|  | DG | [32 empty] | AHU
5 | 3F | SL No 540430038849 (EB Unit) | [32 empty] | BTU
|  | DG | [32 empty] | DG
6 | 3F | SL No 540430038696 (EB Unit)
DG
7 | 3F | SL No 540430038843 (EB Unit)
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3
DG
4 | 3F | AHU4
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## March-25
MARCH-25
Sr.No | Location | Meter | Previous Reading | 2025-03-01 | 2025-03-02 | 2025-03-03 | 2025-03-04 | 2025-03-05 | 2025-03-06 | 2025-03-07 | 2025-03-08 | 2025-03-09 | 2025-03-10 | 2025-03-11 | 2025-03-12 | 2025-03-13 | 2025-03-14 | 2025-03-15 | 2025-03-16 | 2025-03-17 | 2025-03-18 | 2025-03-19 | 2025-03-20 | 2025-03-21 | 2025-03-22 | 2025-03-23 | 2025-03-24 | 2025-03-25 | 2025-03-26 | 2025-03-27 | 2025-03-28 | 2025-03-29 | 2025-03-30 | 2025-03-31 | Consumption
|  |  |  | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 91663 | 92019 | 92228 | 92483 | 92758 | 93012 | 93286 | 93636 | 93844 | 94034 | 94298 | 94563 | 94813 | 95061 | 95269 | 95490 | 95698 | 95996 | 96217 | 96488 | 96760 | 97024 | 97247 | 97452 | 97704 | 97976 | 98245 | 98527 | 98788 | 99006 | 99215 | 99316
|  | DG | 3877 | 3885 | 3885 | 3885 | 3885 | 3885 | 3885 | 3885 | 3902 | 3918 | 3918 | 3918 | 3918 | 3918 | 3923 | 3923 | 3923 | 3923 | 3944 | 3949 | 3949 | 3949 | 3950 | 3950 | 3970 | 3970 | 3970 | 3970 | 3970 | 3970 | 3970 | 3970
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 134648 | 135143 | 135420 | 135791 | 136190 | 136563 | 136964 | 137341 | 137582 | 137874 | 138255 | 138637 | 138999 | 139346 | 139624 | 139918 | 140197 | 140598 | 140959 | 141357 | 141759 | 142145 | 142445 | 142719 | 143091 | 143478 | 143888 | 144308 | 144688 | 144984 | 145266 | 145395
|  | DG | 5807 | 5807 | 5807 | 5817 | 5817 | 5817 | 5817 | 5817 | 5841 | 5861 | 5861 | 5861 | 5861 | 5861 | 5868 | 5868 | 5868 | 5868 | 5901 | 5909 | 5909 | 5909 | 5910 | 5910 | 5938 | 5938 | 5938 | 5938 | 5938 | 5938 | 5938 | 5938
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 62776 | 63047 | 63186 | 63424 | 63679 | 63921 | 64170 | 64420 | 64564 | 64685 | 64891 | 65099 | 65292 | 65468 | 65578 | 65699 | 65818 | 66032 | 66206 | 66400 | 66611 | 66812 | 66913 | 67034 | 67238 | 67467 | 67675 | 67891 | 68095 | 68216 | 68337 | 68389
|  | DG | 2950 | 2955 | 2955 | 2955 | 2955 | 2955 | 2955 | 2955 | 2964 | 2979 | 2979 | 2979 | 2979 | 2979 | 2982 | 2982 | 2982 | 2982 | 2998 | 3002 | 3002 | 3002 | 3002 | 3002 | 3018 | 3018 | 3018 | 3018 | 3018 | 3018 | 3018 | 3018
6 | 3F | SL No 540430038646 (EB Unit) | 76460 | 76728 | 76843 | 77094 | 77355 | 77609 | 77869 | 78107 | 78258 | 78357 | 78627 | 78896 | 79147 | 79393 | 79481 | 79593 | 79687 | 79967 | 80169 | 80444 | 80715 | 80999 | 81129 | 81248 | 81568 | 81850 | 82104 | 82403 | 82644 | 82761 | 82867 | 82927
|  | DG | 3854 | 3861 | 3861 | 3861 | 3861 | 3861 | 3861 | 3861 | 3873 | 3878 | 3878 | 3878 | 3878 | 3878 | 3880 | 3880 | 3880 | 3880 | 3903 | 3908 | 3908 | 3908 | 3909 | 3909 | 3935 | 3935 | 3935 | 3935 | 3935 | 3935 | 3935 | 3935
7 | 3F | SL No 540430038843 (EB Unit) | 255821 | 256803 | 257277 | 257977 | 258722 | 259403 | 260116 | 260841 | 261422 | 261871 | 262604 | 263344 | 264040 | 264777 | 265180 | 265697 | 266152 | 266931 | 267558 | 268273 | 269010 | 269707 | 270276 | 270770 | 271392 | 272110 | 272816 | 273836 | 274528 | 275049 | 275563 | 275737
|  | DG | 10477 | 10503 | 10503 | 10503 | 10503 | 10503 | 10503 | 10503 | 10551 | 10597 | 10597 | 10597 | 10597 | 10597 | 10605 | 10605 | 10605 | 10605 | 10660 | 10671 | 10671 | 10671 | 10673 | 10673 | 10746 | 10746 | 10746 | 10746 | 10746 | 10746 | 10746 | 10746
8 | 3F | SL No 540430038848 (EB Unit) | 51469 | 51720 | 51841 | 52004 | 52141 | 52276 | 52372 | 52483 | 52553 | 52625 | 52798 | 52930 | 53087 | 53217 | 53360 | 53484 | 53625 | 53778 | 53903 | 54020 | 54173 | 54298 | 54450 | 54556 | 54715 | 54827 | 54954 | 55095 | 55249 | 55337 | 55433 | 55458
|  | DG | 2009 | 2012 | 2012 | 2012 | 2012 | 2012 | 2012 | 2012 | 2017 | 2031 | 2031 | 2031 | 2031 | 2031 | 2032 | 2032 | 2032 | 2032 | 2041 | 2041 | 2041 | 2041 | 2042 | 2042 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048 | 2048
1 | 3F | AHU1 | 24020 | 24114 | 24115 | 24179 | 24253 | 24305 | 24339 | 24372 | 24405 | 24405 | 24454 | 24506 | 24551 | 24592 | 24593 | 24614 | 24614 | 24687 | 24731 | 24768 | 24817 | 24865 | 24901 | 24901 | 24948 | 24987 | 25041 | 25094 | 25137 | 25187 | 25187 | 25188
|  | DG | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1824 | 1825 | 1825 | 1825 | 1825 | 1825 | 1832 | 1832 | 1832 | 1832 | 1832 | 1832 | 1832 | 1832
2 | 3F | AHU2 | 24157 | 24260 | 24260 | 24331 | 24385 | 24435 | 24513 | 24594 | 24620 | 24620 | 24696 | 24778 | 24854 | 24932 | 24932 | 24978 | 24978 | 25063 | 25140 | 25211 | 25259 | 25370 | 25438 | 25438 | 25520 | 25604 | 25660 | 25726 | 25803 | 25864 | 25864 | 25865
|  | DG | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1778 | 1780 | 1780 | 1780 | 1780 | 1780 | 1797 | 1797 | 1797 | 1797 | 1797 | 1797 | 1797 | 1797
3 | 3F | AHU3 | 24421 | 24604 | 24604 | 24729 | 24869 | 24998 | 25113 | 25230 | 25297 | 25297 | 25423 | 25557 | 25670 | 25786 | 25786 | 25855 | 25855 | 25982 | 26097 | 26209 | 26309 | 26463 | 26561 | 26561 | 26674 | 26801 | 26880 | 26963 | 27018 | 27081 | 27081 | 27082
|  | DG | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1867 | 1867 | 1867 | 1867 | 1867 | 1867 | 1867 | 1867 | 1867 | 1867 | 1877 | 1880 | 1880 | 1880 | 1881 | 1881 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903 | 1903
4 | 3F | AHU4 | 21969 | 22048 | 22048 | 22099 | 22166 | 22229 | 22279 | 22316 | 22338 | 22338 | 22387 | 22436 | 22498 | 22563 | 22564 | 22588 | 22588 | 22639 | 22694 | 22734 | 22809 | 22858 | 22897 | 22897 | 22960 | 23006 | 23081 | 23133 | 23183 | 23226 | 23226 | 23227
|  | DG | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1677 | 1677 | 1677 | 1677 | 1680 | 1681 | 1681 | 1681 | 1682 | 1682 | 1686 | 1686 | 1686 | 1686 | 1686 | 1686 | 1686 | 1686
1 | 3F | AHU1 - BTU | 204528 | 205133 | 205133 | 206112 | 206840 | 207466 | 208023 | 208582 | 208822 | 208822 | 209692 | 210404 | 211092 | 211747 | 211747 | 212012 | 212012 | 212938 | 213688 | 214429 | 215218 | 215880 | 216242 | 216242 | 217084 | 217901 | 218784 | 219562 | 220306 | 220563 | 220563 | 220563
2 | 3F | AHU2 - BTU | 211729 | 212106 | 212106 | 212711 | 213252 | 213684 | 214137 | 214657 | 214823 | 214823 | 215509 | 216088 | 216763 | 217284 | 217284 | 217527 | 217527 | 218345 | 219030 | 219746 | 220342 | 220845 | 221227 | 221227 | 221901 | 222679 | 223394 | 224038 | 224606 | 224872 | 224872 | 224872
3 | 3F | AHU3 - BTU | 208888 | 209149 | 209149 | 209563 | 209981 | 210276 | 210650 | 211050 | 211211 | 211211 | 211802 | 212283 | 212971 | 213413 | 213413 | 213640 | 213640 | 214360 | 215084 | 215704 | 216215 | 216639 | 216899 | 216899 | 217704 | 218334 | 218949 | 219594 | 220142 | 220395 | 220395 | 220395
4 | 3F | AHU4 - BTU | 230669 | 231224 | 231224 | 231914 | 232513 | 233136 | 233568 | 234049 | 234245 | 234245 | 234949 | 235494 | 236061 | 236609 | 236609 | 236803 | 236803 | 237482 | 238138 | 238792 | 239470 | 240053 | 240371 | 240371 | 241047 | 241709 | 242463 | 243122 | 243810 | 244029 | 244029 | 244029
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time |  | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
|  | DG | [33 empty] | EB
6 | 3F | SL No 540430038696 (EB Unit) | [33 empty] | AHU
|  | DG | [33 empty] | BTU
7 | 3F | SL No 540430038843 (EB Unit) | [33 empty] | DG
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3
DG
4 | 3F | AHU4
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## Feb-2025
October 2024
Sr.No | Location | Meter | Previous Reading | 2025-02-01 | 2025-02-02 | 2025-02-03 | 2025-02-04 | 2025-02-05 | 2025-02-06 | 2025-02-07 | 2025-02-08 | 2025-02-09 | 2025-02-10 | 2025-02-11 | 2025-02-12 | 2025-02-13 | 2025-02-14 | 2025-02-15 | 2025-02-16 | 2025-02-17 | 2025-02-18 | 2025-02-19 | 2025-02-20 | 2025-02-21 | 2025-02-22 | 2025-02-23 | 2025-02-24 | 2025-02-25 | 2025-02-26 | 2025-02-27 | 2025-02-28 | Consumption
|  |  |  | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 84669 | 84989 | 85202 | 85467 | 85732 | 85997 | 86276 | 86534 | 86749 | 86976 | 87236 | 87505 | 87786 | 88057 | 88298 | 88513 | 88724 | 88987 | 89257 | 89533 | 89813 | 90075 | 90295 | 90508 | 90759 | 91026 | 91279 | 91547 | 91663
|  | DG | 3872 | 3872 | 3872 | 3872 | 3872 | 3872 | 3872 | 3872 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877 | 3877
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 124715 | 125147 | 125429 | 125816 | 126203 | 126584 | 126992 | 127364 | 127650 | 127953 | 128334 | 128723 | 129136 | 129533 | 129874 | 130161 | 130437 | 130816 | 131209 | 131615 | 132030 | 132410 | 132706 | 132983 | 133344 | 133729 | 134092 | 134485 | 134648
|  | DG | 5799 | 5799 | 5799 | 5799 | 5799 | 5799 | 5799 | 5799 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807 | 5807
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 56491 | 56749 | 56895 | 57149 | 57409 | 57657 | 57919 | 58155 | 58316 | 58472 | 58724 | 58988 | 59268 | 59544 | 59786 | 59955 | 60100 | 60355 | 60610 | 60888 | 61162 | 61413 | 61547 | 61694 | 61931 | 62190 | 62419 | 62674 | 62776
|  | DG | 2944 | 2944 | 2944 | 2944 | 2944 | 2944 | 2944 | 2944 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950 | 2950
6 | 3F | SL No 540430038646 (EB Unit) | 70440 | 70653 | 70766 | 71014 | 71281 | 71527 | 71798 | 72025 | 72158 | 72255 | 72507 | 72763 | 73042 | 73303 | 73550 | 73692 | 73807 | 74048 | 74319 | 74605 | 74896 | 75153 | 75268 | 75383 | 75626 | 75871 | 76113 | 76357 | 76460
|  | DG | 3848 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854 | 3854
7 | 3F | SL No 540430038843 (EB Unit) | 237024 | 237024 | 237949 | 238433 | 239860 | 240581 | 241338 | 242062 | 242640 | 243103 | 243859 | 244557 | 245291 | 246003 | 246679 | 247284 | 247712 | 248430 | 249169 | 249960 | 250705 | 251513 | 252110 | 252645 | 253335 | 254084 | 254797 | 255530 | 255821
|  | DG | 10460 | 10460 | 10460 | 10460 | 10460 | 10460 | 10460 | 10460 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477 | 10477
8 | 3F | SL No 540430038848 (EB Unit) | 48163 | 48368 | 48484 | 48617 | 48710 | 48855 | 48940 | 49033 | 49121 | 49255 | 49360 | 49494 | 49588 | 49677 | 49748 | 49820 | 49908 | 50013 | 50119 | 50267 | 50414 | 50571 | 50689 | 50836 | 50972 | 51137 | 51270 | 51434 | 51469
|  | DG | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009 | 2009
1 | 3F | AHU1 | 22927 | 22955 | 22955 | 22993 | 23029 | 23065 | 23103 | 23141 | 23180 | 23180 | 23215 | 23253 | 23309 | 23386 | 23447 | 23466 | 23466 | 23515 | 23577 | 23640 | 23700 | 23763 | 23784 | 23784 | 23841 | 23906 | 23964 | 24011 | 24020
|  | DG | 1819 | 1819 | 1819 | 1819 | 1819 | 1819 | 1819 | 1819 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821 | 1821
2 | 3F | AHU2 | 22592 | 22652 | 22652 | 22724 | 22769 | 22813 | 22869 | 22913 | 22939 | 22939 | 23037 | 23090 | 23161 | 23227 | 23320 | 23343 | 23343 | 23407 | 23501 | 23590 | 23681 | 23768 | 23792 | 23792 | 23876 | 23974 | 24067 | 24146 | 24157
|  | DG | 1769 | 1769 | 1769 | 1769 | 1769 | 1769 | 1769 | 1769 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772 | 1772
3 | 3F | AHU3 | 22468 | 22539 | 22539 | 22599 | 22646 | 22693 | 22775 | 22822 | 22846 | 22846 | 22963 | 23012 | 23085 | 23140 | 23229 | 23253 | 23253 | 23317 | 23439 | 23570 | 23709 | 23837 | 23907 | 23907 | 24033 | 24157 | 24219 | 24400 | 24421
|  | DG | 1864 | 1864 | 1864 | 1864 | 1864 | 1864 | 1864 | 1864 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866 | 1866
4 | 3F | AHU4 | 20730 | 20768 | 20768 | 20821 | 20875 | 20928 | 20986 | 21037 | 21064 | 21064 | 21129 | 21182 | 21243 | 21300 | 21349 | 21377 | 21377 | 21443 | 21514 | 21578 | 21647 | 21708 | 21739 | 21739 | 21793 | 21846 | 21905 | 21957 | 21969
|  | DG | 1673 | 1673 | 1673 | 1673 | 1673 | 1673 | 1673 | 1673 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676 | 1676
1 | 3F | AHU1 - BTU | 190977 | 191265 | 191265 | 191840 | 192439 | 192978 | 193507 | 193974 | 194024 | 194024 | 194715 | 195325 | 195900 | 196396 | 196898 | 197123 | 197123 | 197926 | 198630 | 199452 | 200462 | 201194 | 201326 | 201326 | 202187 | 202963 | 203611 | 204264 | 204528
2 | 3F | AHU2 - BTU | 200908 | 201180 | 201180 | 201727 | 202188 | 202642 | 203036 | 203424 | 203454 | 203454 | 204066 | 204619 | 205112 | 205562 | 205915 | 206101 | 206101 | 206773 | 207395 | 207997 | 208676 | 209184 | 209269 | 209269 | 209917 | 210511 | 211056 | 211532 | 211729
3 | 3F | AHU3 - BTU | 200887 | 201182 | 201182 | 201638 | 201951 | 202311 | 202626 | 202871 | 202903 | 202903 | 203369 | 203762 | 204232 | 204631 | 204890 | 204972 | 204972 | 205402 | 205798 | 206161 | 206674 | 207031 | 207119 | 207119 | 207478 | 207887 | 208293 | 208693 | 208888
4 | 3F | AHU4 - BTU | 219082 | 219349 | 219349 | 219911 | 220484 | 221002 | 221519 | 221908 | 221974 | 221974 | 222553 | 223123 | 223619 | 224037 | 224493 | 224696 | 224696 | 225291 | 225900 | 226666 | 227420 | 228088 | 228213 | 228213 | 228875 | 229318 | 229849 | 230433 | 230669
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [29 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
|  | DG | [30 empty] | EB
6 | 3F | SL No 540430038696 (EB Unit) | [30 empty] | AHU
|  | DG | [30 empty] | BTU
7 | 3F | SL No 540430038843 (EB Unit) | [30 empty] | DG
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3
DG
4 | 3F | AHU4
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption

## Jan-2025
October 2024
Sr.No | Location | Meter | Previous Reading | 2025-01-01 | 2025-01-02 | 2025-01-03 | 2025-01-04 | 2025-01-05 | 2025-01-06 | 2025-01-07 | 2025-01-08 | 2025-01-09 | 2025-01-10 | 2025-01-11 | 2025-01-12 | 2025-01-13 | 2025-01-14 | 2025-01-15 | 2025-01-16 | 2025-01-17 | 2025-01-18 | 2025-01-19 | 2025-01-20 | 2025-01-21 | 2025-01-22 | 2025-01-23 | 2025-01-24 | 2025-01-25 | 2025-01-26 | 2025-01-27 | 2025-01-28 | 2025-01-29 | 2025-01-30 | 2025-01-31 | Consumption
|  |  |  | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI | SAT | SUN | MON | TUE | WED | THU | FRI
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit) | 76944 | 77277 | 77495 | 77717 | 77950 | 78153 | 78415 | 78684 | 78951 | 79208 | 79459 | 79678 | 79898 | 80134 | 80382 | 80665 | 80928 | 81192 | 81413 | 81640 | 81911 | 82182 | 82432 | 82692 | 82938 | 83170 | 83390 | 83637 | 83900 | 84177 | 84536 | 84669
|  | DG | 3801 | 3801 | 3801 | 3801 | 3801 | 3801 | 3801 | 3801 | 3801 | 3801 | 3801 | 3801 | 3801 | 3839 | 3839 | 3839 | 3839 | 3839 | 3839 | 3842 | 3853 | 3853 | 3872 | 3872 | 3872 | 3872 | 3872 | 3872 | 3872 | 3872 | 3872 | 3872
2 | 3F | SL No 540430038845 (EB Unit) | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956 | 1956
|  | DG | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
3 | 3F | SL No 540430038844 (EB Unit) | 113760 | 114205 | 114499 | 114807 | 115107 | 115375 | 115754 | 116208 | 116591 | 116962 | 117320 | 117614 | 117905 | 118250 | 118609 | 119016 | 119557 | 119938 | 120235 | 120534 | 120905 | 121297 | 121661 | 122041 | 122388 | 122699 | 122981 | 123348 | 123721 | 124131 | 124527 | 124715
|  | DG | 5702 | 5702 | 5702 | 5702 | 5702 | 5702 | 5702 | 5702 | 5702 | 5702 | 5702 | 5702 | 5702 | 5751 | 5751 | 5751 | 5751 | 5751 | 5751 | 5755 | 5772 | 5772 | 5799 | 5799 | 5799 | 5799 | 5799 | 5799 | 5799 | 5799 | 5799 | 5799
4 | 3F | SL No 540430038821 (EB Unit) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | DG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 3F | SL No 540430038849 (EB Unit) | 50207 | 50396 | 50555 | 50714 | 50843 | 50956 | 51189 | 51412 | 51646 | 51876 | 52136 | 52284 | 52415 | 52635 | 52868 | 53117 | 53360 | 53604 | 53749 | 53892 | 54134 | 54391 | 54637 | 54880 | 55101 | 55229 | 55385 | 55624 | 55859 | 56105 | 56363 | 56491
|  | DG | 2892 | 2892 | 2892 | 2892 | 2892 | 2892 | 2892 | 2892 | 2892 | 2892 | 2892 | 2892 | 2892 | 2914 | 2914 | 2914 | 2914 | 2914 | 2914 | 2917 | 2927 | 2927 | 2944 | 2944 | 2944 | 2944 | 2944 | 2944 | 2944 | 2944 | 2944 | 2944
6 | 3F | SL No 540430038646 (EB Unit) | 64448 | 64614 | 64745 | 64881 | 64987 | 65080 | 65301 | 65547 | 65793 | 65999 | 66206 | 66310 | 66405 | 66619 | 66829 | 67072 | 67301 | 67538 | 67632 | 67751 | 68016 | 68288 | 68542 | 68818 | 69067 | 69211 | 69300 | 69566 | 69788 | 70046 | 70296 | 70440
|  | DG | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3800 | 3821 | 3821 | 3821 | 3821 | 3821 | 3821 | 3823 | 3835 | 3835 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848 | 3848
7 | 3F | SL No 540430038843 (EB Unit) | 217622 | 218306 | 218837 | 219434 | 219880 | 220289 | 221010 | 221753 | 222497 | 223201 | 223908 | 224521 | 224967 | 225615 | 226304 | 227060 | 227779 | 228501 | 229044 | 229473 | 230165 | 230880 | 231544 | 232214 | 232885 | 233482 | 233863 | 234519 | 235231 | 235956 | 236711 | 237024
|  | DG | 10322 | 10322 | 10322 | 10322 | 10322 | 10322 | 10322 | 10322 | 10322 | 10322 | 10322 | 10322 | 10322 | 10389 | 10389 | 10389 | 10389 | 10389 | 10389 | 10395 | 10420 | 10420 | 10460 | 10460 | 10460 | 10460 | 10460 | 10460 | 10460 | 10460 | 10460 | 10460
8 | 3F | SL No 540430038848 (EB Unit) | 45289 | 45401 | 45482 | 45568 | 45656 | 45725 | 45810 | 45884 | 45963 | 46033 | 46115 | 46186 | 46266 | 46332 | 46419 | 46502 | 46595 | 46704 | 46797 | 46899 | 47038 | 47165 | 47281 | 47404 | 47548 | 47645 | 47743 | 47834 | 47940 | 48034 | 48133 | 48163
|  | DG | 1985 | 1985 | 1985 | 1985 | 1985 | 1985 | 1985 | 1985 | 1985 | 1985 | 1985 | 1985 | 1985 | 1992 | 1992 | 1992 | 1992 | 1992 | 1992 | 1993 | 1998 | 1998 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007 | 2007
1 | 3F | AHU1 | 21831 | 21831 | 21887 | 21926 | 21932 | 21932 | 21980 | 22015 | 22049 | 22085 | 22124 | 22156 | 22156 | 22196 | 22249 | 22302 | 22351 | 22399 | 22417 | 22417 | 22488 | 22545 | 22600 | 22662 | 22707 | 22728 | 22728 | 22769 | 22806 | 22842 | 22892 | 22927
|  | DG | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1811 | 1815 | 1815 | 1819 | 1819 | 1819 | 1819 | 1819 | 1819 | 1819 | 1819 | 1819 | 1819
2 | 3F | AHU2 | 21457 | 21457 | 21507 | 21554 | 21559 | 21559 | 21602 | 21630 | 21660 | 21699 | 21731 | 21754 | 21754 | 21784 | 21818 | 21881 | 21926 | 21974 | 21989 | 21989 | 22057 | 22099 | 22132 | 22195 | 22243 | 22268 | 22268 | 22318 | 22365 | 22445 | 22547 | 22592
|  | DG | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1765 | 1767 | 1767 | 1767 | 1767 | 1767 | 1767 | 1767 | 1767 | 1767 | 1767 | 1767 | 1767
3 | 3F | AHU3 | 21190 | 21190 | 21222 | 21233 | 21243 | 21243 | 21306 | 21352 | 21397 | 21442 | 21491 | 21530 | 21530 | 21578 | 21647 | 21740 | 21802 | 21886 | 21889 | 21889 | 21950 | 21951 | 22034 | 22078 | 22119 | 22143 | 22143 | 22187 | 22229 | 22301 | 22416 | 22468
|  | DG | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1859 | 1861 | 1861 | 1864 | 1864 | 1864 | 1864 | 1864 | 1864 | 1864 | 1864 | 1864 | 1864
4 | 3F | AHU4 | 19720 | 19720 | 19722 | 19722 | 19727 | 19727 | 19775 | 19817 | 19858 | 19899 | 19945 | 19960 | 19960 | 20004 | 20072 | 20142 | 20198 | 20251 | 20263 | 20263 | 20325 | 20365 | 20410 | 20454 | 20496 | 20500 | 20500 | 20534 | 20567 | 20626 | 20680 | 20730
|  | DG | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1668 | 1671 | 1671 | 1673 | 1673 | 1673 | 1673 | 1673 | 1673 | 1673 | 1673 | 1673 | 1673
1 | 3F | AHU1 - BTU | 180287 | 180287 | 180602 | 180739 | 180806 | 180806 | 181385 | 181840 | 182294 | 182720 | 183099 | 183223 | 183223 | 183613 | 184044 | 184481 | 184780 | 185168 | 185300 | 185300 | 185975 | 186606 | 187122 | 187723 | 188169 | 188342 | 188342 | 188941 | 189477 | 190008 | 190510 | 190977
2 | 3F | AHU2 - BTU | 192836 | 192836 | 192959 | 193151 | 193177 | 193177 | 193510 | 193787 | 194107 | 194529 | 194760 | 194877 | 194877 | 195116 | 195338 | 195619 | 195891 | 196174 | 196321 | 196321 | 196795 | 197253 | 197689 | 198155 | 198556 | 198704 | 198704 | 199202 | 199722 | 200149 | 200595 | 200908
3 | 3F | AHU3 - BTU | 194316 | 194316 | 194345 | 194364 | 194385 | 194385 | 194540 | 194818 | 195282 | 195767 | 196021 | 196145 | 196145 | 196448 | 196567 | 196746 | 196947 | 197284 | 197484 | 197484 | 197852 | 198113 | 198544 | 199084 | 199311 | 199405 | 199705 | 199679 | 199959 | 200249 | 200612 | 200887
4 | 3F | AHU4 - BTU | 211795 | 211806 | 211812 | 211815 | 211820 | 211820 | 212056 | 212229 | 212560 | 212999 | 213101 | 213107 | 213107 | 213261 | 213434 | 213615 | 213825 | 214148 | 214227 | 214227 | 214826 | 215348 | 215793 | 216288 | 216693 | 216778 | 216778 | 217299 | 217763 | 218251 | 218678 | 219082
Daily Energy Report
Electricity Consumption
Sr.No | Location | Meter | [32 empty] | Consumption
|  |  |  | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time | Time |  | Time
|  |  |  | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00 | 8:00
1 | 3F | SL No 540430038840 (EB Unit)
DG
2 | 3F | SL No 540430038845 (EB Unit)
DG
3 | 3F | SL No 540430038844 (EB Unit)
DG
4 | 3F | SL No 540430038821 (EB Unit)
DG
5 | 3F | SL No 540430038849 (EB Unit)
|  | DG | [33 empty] | EB
6 | 3F | SL No 540430038696 (EB Unit) | [33 empty] | AHU
|  | DG | [33 empty] | BTU
7 | 3F | SL No 540430038843 (EB Unit) | [33 empty] | DG
DG
8 | 3F | SL No 540430038848 (EB Unit)
DG
Total Power - EB Unit
Total Power- DG
Total Power Cumulative
S No | Location | Meter
1 | 3F | AHU1
DG
2 | 3F | AHU2
DG
3 | 3F | AHU3
DG
4 | 3F | AHU4
DG
Total AHU Power Consumption
Total AHU DG consumption
1 | 3F | AHU1 - BTU
2 | 3F | AHU2 - BTU
3 | 3F | AHU3 - BTU
4 | 3F | AHU4 - BTU
Total BTU Consumption